## Overview
Overview
BIMids filters |  | Disclaimer
FILTERS | VALUE | As this file can be modified, we cannot guarantee that this document conforms to the content of the BIMids platform. If the user makes any changes, these must be clearly highlighted.
Version | wip
Language | English
Country | Belgium
Disciplines | Architecture, MEP, Structure
Use-cases | Minimum requirements, Programming (partial requirements), Architectural design (partial requirements), Structural design (partial requirements), Sanitary/HVAC design (partial requirements), Electrical design (partial requirements), Handicap accessibility (partial requirements), Fire safety (partial requirements), Rendering (partial requirements), PEB (partial requirements), Acoustics (partial requirements), Building permit (partial requirements), Heat loss calculation, Intrusion and surveillance (partial requirements), 2D documents (partial requirements), Precasting (partial requirements), Clash detection (partial requirements), Access management (partial requirements), Maintenance (partial requirements), LCA (Life Cycle Analysis), Optional requirements
IFC Versions | IFC 2X3 TC1, IFC 4 Add2, IFC 4.3
Software | -
Export Date | 12/09/2024
Elements
ELEMENT | BIMIDS LINK
Actuator | https://www.bimids.eu/be-en/elements/actuator?version=wip
Air handling unit | https://www.bimids.eu/be-en/elements/air-handling-unit?version=wip
Air-to-air exchanger | https://www.bimids.eu/be-en/elements/air-to-air-exchanger?version=wip
Audiovisual device | https://www.bimids.eu/be-en/elements/audiovisual-device?version=wip
Beam | https://www.bimids.eu/be-en/elements/beam?version=wip
Breeching inlet | https://www.bimids.eu/be-en/elements/breeching-inlet?version=wip
Cable tray | https://www.bimids.eu/be-en/elements/cable-tray?version=wip
Cable tray connection | https://www.bimids.eu/be-en/elements/cable-tray-connection?version=wip
Caisson foundation | https://www.bimids.eu/be-en/elements/caisson-foundation?version=wip
Ceiling finishing | https://www.bimids.eu/be-en/elements/ceiling-finishing?version=wip
Chiller | https://www.bimids.eu/be-en/elements/cold-production?version=wip
Chimney | https://www.bimids.eu/be-en/elements/chimney?version=wip
Column | https://www.bimids.eu/be-en/elements/column?version=wip
Curtain wall | https://www.bimids.eu/be-en/elements/curtain-wall?version=wip
Damper and register | https://www.bimids.eu/be-en/elements/damper-and-register?version=wip
Data device | https://www.bimids.eu/be-en/elements/data-device?version=wip
Deep foundation | https://www.bimids.eu/be-en/elements/deep-foundation?version=wip
Door | https://www.bimids.eu/be-en/elements/door?version=wip
Electric appliance | https://www.bimids.eu/be-en/elements/electric-appliance?version=wip
Electrical generator | https://www.bimids.eu/be-en/elements/electrical-generator?version=wip
Electrical outlet | https://www.bimids.eu/be-en/elements/electrical-outlet?version=wip
Electrical panel | https://www.bimids.eu/be-en/elements/electrical-panel?version=wip
Electrical protection equipment | https://www.bimids.eu/be-en/elements/electrical-protection-equipment?version=wip
Electrical switch | https://www.bimids.eu/be-en/elements/electrical-switch?version=wip
Electrical transformer | https://www.bimids.eu/be-en/elements/electrical-transformer?version=wip
Electricity storage | https://www.bimids.eu/be-en/elements/electricity-storage?version=wip
Extinguisher | https://www.bimids.eu/be-en/elements/extinguisher?version=wip
False ceiling | https://www.bimids.eu/be-en/elements/suspended-ceiling?version=wip
Fan | https://www.bimids.eu/be-en/elements/fan?version=wip
Filter | https://www.bimids.eu/be-en/elements/filter?version=wip
Fire hose reel | https://www.bimids.eu/be-en/elements/fire-hose-reel?version=wip
Fire hydrant | https://www.bimids.eu/be-en/elements/fire-hydrant?version=wip
Fire protection cabinet | https://www.bimids.eu/be-en/elements/fire-protection-cabinet?version=wip
Floor finishing | https://www.bimids.eu/be-en/elements/floor-finishing?version=wip
Foundation beam | https://www.bimids.eu/be-en/elements/foundation-beam?version=wip
Foundation footing | https://www.bimids.eu/be-en/elements/foundation-footing?version=wip
Furniture | https://www.bimids.eu/be-en/elements/furniture?version=wip
Heat diffusion - radiator | https://www.bimids.eu/be-en/elements/heat-diffusion-radiator?version=wip
Heat production - steam | https://www.bimids.eu/be-en/elements/heat-production-steam?version=wip
Heat production - water | https://www.bimids.eu/be-en/elements/heat-production-water?version=wip
Heat/cold diffusion - surface | https://www.bimids.eu/be-en/elements/heat-cold-diffusion-surface?version=wip
Heat/cold distribution - convector | https://www.bimids.eu/be-en/elements/heat-cold-distribution-convector?version=wip
Lift | https://www.bimids.eu/be-en/elements/lift?version=wip
Lightfixture | https://www.bimids.eu/be-en/elements/light-fixture?version=wip
Linear structural member | https://www.bimids.eu/be-en/elements/linear-structural-member?version=wip
Management panel | https://www.bimids.eu/be-en/elements/management-panel?version=wip
Pump | https://www.bimids.eu/be-en/elements/pump?version=wip
Ramp | https://www.bimids.eu/be-en/elements/ramp?version=wip
Roof | https://www.bimids.eu/be-en/elements/roof?version=wip
Roof finishing | https://www.bimids.eu/be-en/elements/roof-finishing?version=wip
Safety lighting | https://www.bimids.eu/be-en/elements/safety-lighting?version=wip
Sanitary equipment | https://www.bimids.eu/be-en/elements/sanitary-equipment?version=wip
Sanitary/heating pipe | https://www.bimids.eu/be-en/elements/sanitary-heating-pipe?version=wip
Sanitary/heating pipe fitting | https://www.bimids.eu/be-en/elements/sanitary-heating-pipe-fitting?version=wip
Slab | https://www.bimids.eu/be-en/elements/slab?version=wip
Slab-on-grade | https://www.bimids.eu/be-en/elements/slab-on-grade?version=wip
Solar panel | https://www.bimids.eu/be-en/elements/solar-panel?version=wip
Space | https://www.bimids.eu/be-en/elements/space?version=wip
Sprinkler | https://www.bimids.eu/be-en/elements/sprinkler?version=wip
Stair | https://www.bimids.eu/be-en/elements/stair?version=wip
Tank | https://www.bimids.eu/be-en/elements/tank?version=wip
Technical floor | https://www.bimids.eu/be-en/elements/technical-floor?version=wip
Transport equipment (excluding lifts) | https://www.bimids.eu/be-en/elements/transport-equipment?version=wip
Ventilation air terminal | https://www.bimids.eu/be-en/elements/ventilation-air-terminal?version=wip
Ventilation duct | https://www.bimids.eu/be-en/elements/ventilation-duct?version=wip
Ventilation duct connection | https://www.bimids.eu/be-en/elements/ventilation-duct-connection?version=wip
Ventilation silencer | https://www.bimids.eu/be-en/elements/ventilation-silencer?version=wip
Wall | https://www.bimids.eu/be-en/elements/wall?version=wip
Wall finishing | https://www.bimids.eu/be-en/elements/wall-finishing?version=wip
Water collector | https://www.bimids.eu/be-en/elements/water-collector?version=wip
Window | https://www.bimids.eu/be-en/elements/window?version=wip
Zone | https://www.bimids.eu/be-en/elements/zone?version=wip

## Use-cases
Use-cases
CODE | NAME | DESCRIPTION
UC 00 | Minimum requirements | The minimum requirements include the basic needs for any BIM project. The requirements included are the common needs without the implementation of other more specific BIM use cases.
UC 01 | Programming (partial requirements) | (Partial requirements for this use case) The use-case of the BIM model to analyse and define the functional and spatial requirements of a construction project prior to design. This includes gathering data on user needs and project requirements to inform design decisions and costs.
UC 02 | Architectural design (partial requirements) | (Partial requirements for this use case) Use-case consisting of modelling an "architectural" model to define spaces and architectural elements. This model will evolve throughout the project and will serve as a basis for the work of the engineers during the technical and structural studies.
UC 03 | Structural design (partial requirements) | (Partial requirements for this use case) Use-case consisting of modelling a "structural" model to define the structural elements of the structure. This model will evolve throughout the project and will be used as a basis for structural studies.
UC 04 | Sanitary/HVAC design (partial requirements) | (Partial requirements for this use case) Use-case consisting of modelling an "HVAC" BIM model to define the technical sanitary and ventilation elements of the structure. This model will evolve throughout the project and will be used as a basis for technical studies.
UC 05 | Electrical design (partial requirements) | (Partial requirements for this use case) Use-case consisting of modelling an "electrical" BIM model to define the electrical components. This model will evolve throughout the project and will be used as a basis for technical studies.
UC 06 | Handicap accessibility (partial requirements) | (Partial requirements for this use case) Use-case consisting of simulating, optimising and verifying on the BIM model the project's compliance with applicable standards on building accessibility for people with disabilities (reduced mobility - PRM, vision, hearing, etc.).
UC 07 | Fire safety (partial requirements) | (Partial requirements for this use case) Use-case consisting of simulating, optimising and checking the project's compliance with applicable building fire safety standards on the model.
UC 08 BE | Rendering (partial requirements) | (Partial requirements for this use case) Use-case consisting of generating realistic images and animations from a BIM model using textures, shapes, etc., with the aim of creating an aesthetic rendering of the structure, used to visualise and communicate the design. This is done in order to establish an aesthetic rendering of the work, used for visualising and communicating the design.
UC 09 BE | PEB (partial requirements) | (Partial requirements for this use case) Use-case consisting of providing information relating to the EPB (energy performance of buildings) based on the European directive on the energy performance of buildings. It enables the overall energy consumption of a building to be calculated, based on the thermal transmittance of its materials and the energy consumed by ventilation, heating, etc.
UC 11 | Acoustics (partial requirements) | (Partial requirements for this use case) Use-case consisting of of simulating, optimising and checking the project's compliance with applicable acoustic standards in the BIM model. For the moment, the only requirement is the acoustic attenuation of walls/slabs/roofs/doors/windows between spaces and from the outside.
UC 13 BE | Building permit (partial requirements) | (Partial requirements for this use case) Use-case consisting of entering information relating to the submission of planning permission. This data will be used to check compliance with local standards.
UC 14 | Heat loss calculation | Use-case consisting of using a BIM model to calculate the power required to heat a building or a room in the coldest conditions. This calculation is carried out prior to sizing a heating system.
UC 15 BE | Intrusion and surveillance (partial requirements) | (Partial requirements for this use case) Use-case consisting of providing information relating to the surveillance of structures and the prevention of intrusion. This improves safety by visualising and optimising surveillance coverage.
UC 16 BE | 2D documents (partial requirements) | (Partial requirements for this use case) Use-case consisting of producing 2D deliverables of a project (plans of all kinds, sections, elevations) generated from the BIM model.
UC 17 | Precasting (partial requirements) | (Partial requirements for this use case) Use-case consisting of modelling and optimising the prefabrication of construction elements.
UC 18 BE | Clash detection (partial requirements) | (Partial requirements for this use case) Use-case consisting of identifying relevant interferences between different building elements in a 3D model prior to construction.
UC 19 | Access management (partial requirements) | (Partial requirements for this use case) Use-case consisting of simulating user access rights in a building in the BIM model and checking that requirements and constraints have been properly defined.
UC 20 BE | Maintenance (partial requirements) | (Partial requirements for this use case) Use-case consisting of using information from the BIM model to plan and manage the maintenance activities of a building. This optimises interventions, reduces costs and extends the life of equipment. This ensures efficient and proactive infrastructure management.
UC 21 BE | LCA (Life Cycle Analysis) | Through a life cycle analysis (LCA) it is possible to map the environmental impact of a building/asset. The insights obtained allow the impact on climate and environment to be reduced and to communicate about it in an objective manner.
UC 99 | Optional requirements | These requirements are optional, so you can use them in your project if you need to. For automatic verification, you will find a check file specific to these optional requirements.

## Property definitions
Property definitions
FILTERS | BIMids property | VALUE
Geometry
Information
Acoustic resistance |  | Indicates the resistance of sound transmission through this object.
Activation temperature |  | Defines the temperature at which the object is designed to activate.
Air temperature (cooling) |  | Indicates the supply air temperature in cooling mode.
Air temperature (heating) |  | Indicates the supply air temperature in heating mode.
Airflow type |  | Describes the type of airflow that the equipment produces.
Backup system |  | Indicates the type of backup supply system.
Bulletproof | x | Indicates the resistance of the door against bullet passage (according to STS 53.1)
Cabin depth |  | Gives the clear depth of the object (elevator). It indicates the distance from the inner surface of the elevator door to the opposite surface of the elevator car.
Cabin height |  | Gives the clear height of the object (elevator).
Cabin width |  | Gives the clear width of the object (elevator). It indicates the distance from the inner surfaces of the elevator car left and right from the elevator door.
Cabinet with lock |  | Indicates whether the file cabinet is lockable (TRUE) or not (FALSE).
Capacity |  | Gives the product of the ideal capacity and the overall volumetric efficiency of the compressor.
Capacity flush (volume) |  | Gives the volumetric capacity of the flush.
Capacity in persons |  | Indicates the capacity of the transportation element measured in numbers of person.
Capacity in weight |  | Indicates the capacity of the transport element measured by weight.
Ceiling finishing |  | Indicates the ceiling finish material if not modelled separately.
Condition - Condition assessed |  | Gives the overall condition of a product based on an assessment of the contributions to the overall condition made by the various criteria considered. The meanings given to the values of assessed condition should be agreed and documented by local agreements. For instance, is overall condition measured on a scale of 1 - 10 or by assigning names such as Good, OK, Poor.
Condition - Date of evaluation |  | Indicates the date on which the overall condition was assessed.
Connection size |  | Indicates the size of the pump connections.
Construction method |  | Defines whether the concrete element is constructed on site (IN-SITU) or prefabricated (PRECAST).
Convector type |  | Indicates the type of convector, whether forced air (mechanically driven) or natural (gravity).
Covered area |  | Defined the area the sprinkler is designed to protect.
Current |  | Indicates the current that a device is designed to handle.
Description |  | Describes the use of the furniture.
Diameter |  | Indicates the bore of the hose.
Direction of the emergency picto |  | Indicates the direction of escape pictogram.
Documentation | x | Indicates the link to the documentation related to the element.
Effective load |  | Indicates the boiler real load.
Effective volume |  | Indicates the effective (real) volume of the tank.
Electrical power |  | Defines the power of the luminaire.
End date of guarantee |  | Indicates the date on which the warranty expires.
Energy consumption |  | Defines the energy consumption of the boiler.
Energy efficiency |  | Defines the operational efficiency of the cooling unit: cooling output divided by the total energy input (electrical and fuel).
Fire rating |  | Also called "fire resistance". Describes the ability of a building component to maintain, for a specified period of time, load-bearing capacity (R), integrity (E), insulation (I) and/or any other required function. In general, the fire resistance classes are expressed as follows: REI t, R t, EI t, E t, S t, where t is the period expressed in minutes.
Fire risk factor |  | Defines,according to local building regulations, the fire risk of the space at several levels of fire hazard.
Flammability rating |  | Also called "reaction to fire". Determines the way a material reacts when it comes into contact with a contact with a contact with heat source. The reaction-to-fire requirements for construction products products are described according to the classification classification (main classes and sub-classes smoke production and flaming droplet formation. formation) from NBN EN 13501-1/ILNAS-EN 13501-1. Remarks : - the requirements in this respect relate to the final application value application value (thus taking into account the presence of the presence of any underlying (flammable) materials).
Floor finishing |  | Indicates the floor finish material in case it is not modelled separately.
Flow rate range |  | Indicates the allowable pumping rate range in relation to the resistance.
Flush type |  | Indicates which type of flush the toilet is equipped with.
Glass layers |  | Indicates the number of glass layers within the frame. E.g. "2" for double glazing.
Glazing area fraction |  | Indicates the fraction of the glazing area relative to the total area of the frame.
Has access control | x | Indicates whether the door is equipped with door access control (badge or code, etc.) (TRUE) or not (FALSE).
Has caps |  | Indicates if the inlet connection has protective caps.
Has diffuser |  | Indication of whether the sprinkler has a deflector (baffle) fitted to diffuse the discharge on activation (TRUE) or not (FALSE).
Has external sill |  | Indicates whether the window opening has an external sill (TRUE) or not (FALSE).
Has internal sill |  | Indicates whether the window opening has an internal sill (TRUE) or not (FALSE).
Has motorized opening |  | Indicates whether the door is equipped with automatic closing (TRUE) or not (FALSE).
Has sprinklers |  | Indicates whether the space is sprinkler protected (TRUE) or not (FALSE).
Has tray |  | Indicates whether the shower has a tray (TRUE) or not (FALSE).
Humidity summer (cooling) |  | Defines the required relative humidity of the space or area in summer. Specified by the user or designer and used as a set point for cooling.
Humidity winter (heating) |  | Defines the required relative humidity of the space or area in winter. Specified by the user or designer and used as a set point for heating.
IFC Object Type |  | Defines the object type if the type is USERDEFINED. This gives an additional indication of the type of object.
IFC Type |  | Defines the specific information about IFC type which is a subtype of the IFC class.
Inlet diameter |  | Indicates the inlet diameter of the breeching inlet.
Is automatic |  | Indicates whether flushing is activated automatically after each use or periodically (TRUE) or whether manual flushing is required (FALSE).
Is automatic shading device | x | Indicates whether the blackout device is automatic (TRUE) or not (FALSE)
Is emergency exit |  | Indication whether this object is designed to serve as an exit in the case of fire (TRUE) or not (FALSE). Here it defines an exit door in accordance to the national building code.
Is emergency exit area |  | Indicates whether this space is an emergency exit (TRUE) or not (FALSE).
Is external |  | Indication whether the element is designed for use in the exterior (TRUE) or not (FALSE). If TRUE it is an external element that supports the weather conditions (cold, humidity, rain,...)
Is external (Archicad) |  | Indication whether the element is designed for use in the exterior (TRUE) or not (FALSE). If TRUE it is an external element and faces the outside of the building.
Is firemen access |  | Indicates whether the elevator is designed to serve as a fire fighting lift the case of fire (TRUE) or not (FALSE).
Is handicap accessible |  | Indicates whether the element is designed to be accessible to the disabled (TRUE) or not (FALSE). This information is often used to declare the need for disabled access or for special design constraints.
Is load-bearing |  | Indicates whether the object is intended to carry loads (TRUE) or not (FALSE).
Is load-bearing (Archicad) |  | Indicates whether the element is intended to carry loads (TRUE) or not (FALSE).
Is load-bearing (Revit) |  | Indicates whether the element is intended to carry loads (TRUE) or not (FALSE).
Is mobile shading device | x | Indicates whether the blackout device is movable (TRUE) or not (FALSE)
Is outer shell | x | Determines whether the element is part of the external envelope of the building (TRUE) or not (FALSE). In other words whether it is an element between the heated volume and the external environment.
Is physically attached |  | Indicates whether the furniture type is 'built in' physically attached to a building or facility (TRUE) or movable (FALSE).
Is public accessible |  | Indication whether this space (in case of e.g., a toilet) is designed to serve as a publicly accessible space, e.g., for a public toilet (TRUE) or not (FALSE).
Length |  | Indicates the length of the hose fitted to the hose reel when fully extended.
Light switch |  | Indicates whether the switch is equipped with an indicator light (TRUE) or not (FALSE).
Luminous flux |  | Indicates the amount of light energy emitted by the source.
Maintenance factor |  | Defines the calculation made for the depreciation of lamps and reflective equipment from their original value due to dirt, smoke or age.
Material |  | The basic entity for naming and defining materials; this includes identification by name and classification (by reference to an external classification), as well as the association of material properties (isotropic or anisotropic) defined by (subtypes of) IfcMaterialProperties. An instance of IfcMaterial can be associated with an element or an element type using the IfcRelAssociatesMaterial relationship.
Maximum cooling temperature |  | Defines the maximal temperature of the space or zone allowed for the hot (summer) period, that is required from user/designer view point and provided as requirement for cooling.
Maximum heating temperature |  | Defines the maximum temperature of the space or area allowed in winter. Specified by the user or designer and used as a set point for heating.
Maximum output power |  | Indicates the maximum output power rating of the engine.
Maximum pressure |  | Indicates the maximum pressure that the hydrant is manufactured to withstand.
Measured air volume flow |  | Indicates the actual airflow measured on site.
Mechanical ventilation required |  | Indicates the requirement of a particular mechanical air ventilation rate, given in air changes per hour.
Minimum cooling temperature |  | Defines the minimum temperature of the space or area allowed in summer. Specified by the user or designer and used as a set point for cooling.
Minimum headroom |  | Headroom required for the activity assigned to this space.
Minimum heating temperature |  | Defines the minimum temperature of the space or area allowad in winter. Specified by the user or designer and used as a set point for heating.
Mounting type | x | Identifies reel type.
Net programmed area |  | Indicates the total planned net area for the space. Used for programming the space.
Nominal air flow |  | Indicates the actual airflow rate as designed.
Nominal efficiency (steam) |  | Defines the total efficiency of the steam heat production equipment as defined by the manufacturer.
Nominal efficiency (water) |  | Defines the total efficiency of the water heat production equipment as defined by the manufacturer.
Nominal electric power |  | Indicates the manufacturer's expected energy consumption.
Nominal flow |  | Specifies the airflow as designed.
Nominal heat output (steam) |  | Defines the total nominal heat output as listed by the steam boiler manufacturer.
Nominal heat output (water) |  | Defines the total nominal heat output as listed by the water boiler manufacturer.
Nominal power |  | Indicates the nominal power of the cooling unit.
Nominal supply voltage |  | Gives the nominal voltage of the supply.
Nominal volume |  | Indicates the nominal volume of the tank.
Number of buttons |  | Gives the number of gangs/buttons on this switch.
Number of connections |  | Indicates the number of hose connections on the hydrant (excluding the pumper connection).
Number of ducts |  | Indicates the number of the chimney drafts, continuous holes in the chimney through which the air passes.
Numerical identifier |  | Identification code that can be read by the human eye (preferably unique to the type of element in the project), such as a door number.
Object name |  | Name of the element/sub-element (preferably unique in the project).
Occupancy number |  | Indicates the number of people required for the activity assigned to this space.
Occupancy type |  | Defines the intended use of the space.
Opening type | x | Indication of the requirement of types of window panel operations. Note : although there is an "IfcWindowPanelProperties" property, some softwares do not export sub-component properties. This property has therefore been transferred to the global element.
Operation type |  | Define the way the door opens. In IFC 2x3, this property is defined at the panel level (IfcDoorPanel) and not at the door level. In some viewer, you need to select the subcomponant of the door, the doorpanel to see this property.
Operational efficiency |  | Defines the operational efficiency of the boiler : heat output divided by the total energy input (electrical and fuel).
Outlet diameter |  | Indicates the outlet diameter of the breeching inlet.
Passage width | x | Indicates the net passage width.
Performance |  | Indicates the ratio of output capacity to intake capacity.
Phasing | x | Determines the phase during which the element is implemented (if the project is carried out in several phases).
Place of assembly |  | Indicates where the assembly of the element should take place, either in the factory or on site.
Placement |  | Defines the type of placing.
Power source |  | Defines the energy source used by the equipment.
Radiator type |  | Indicates the type of radiator.
Recessed |  | Indicates whether the device is recessed (RECESSED) or put on surface (SURFACE).
Reinforcement ratio |  | Indicates the ratio of the reinforcement mass (kg) to the (m³) of the concrete element.
Renovation status (Archicad) |  | Indicates the status of the element, predominantly used in renovation or retrofitting projects. The status can be assigned as "New" - element designed as new addition, "Existing" - element exists and remains, "Demolish" - element existed but is to be demolished, "Temporary" - element will exist only temporarily (like a temporary support structure).
Required illumination |  | Defines the required average illuminance value for this space (lux, lx = Lumens/m²).
Required natural ventilation |  | Indicates the requirement of a particular natural air ventilation rate, given in air changes per hour.
Security rating |  | Indicates the resistance of the door to static and dynamic forces and human human attack.
Sensible cooling capacity |  | Gives the sensible capacity is the ability of the air conditioner to reduce temperature, while the latent capacity is its ability to remove moisture.
Skirtingboard finishing |  | Indicates the material of the skirting boards if not modelled separately.
Solar transmission of glazing |  | Indicates the incident solar radiation that is transmitted directly through the glazing.
Space name |  | Space name holds the full name of the space, it is often used in addition to the number.
Space number |  | Space number holds the unique space number from the plan
Status |  | Indicates the status of the spaces and zones, predominantly used in renovation or retrofitting projects. The status can be assigned as "New" - element designed as new addition, "Existing" - element exists and remains, "Demolish" - element existed but is to be demolished, "Temporary" - element will exist only temporarily (like a temporary support structure).
Switch function |  | Indicates the type of switching of the switch.
Thermal conductivity |  | Determines the thermal conductivity (λ-value) of a material, expressed in W/(mK).
Thermal transmittance |  | Defines the overall heat transfer coefficient through the wall in the direction of heat flow (all materials included) (U-value).
Total effectiveness |  | Or coefficient of performance. It describes the ratio between the energy used and the heat produced
Transformer power |  | Indicates the power of the transformer.
Type activation |  | Defines the type of sprinkler activation.
Type connection |  | Indicates whether the device is connected using a free plug (TRUE), whether it is directly connected (FALSE) or whether the connection is unknown (UNKOWN).
Type hydrant |  | Defines the type of hydrant.
Type of blackout device | x | Specifies the type of sun protection the door or window has.
Type of coupler |  | Defines the type of breeching inlet.
Type of coupling |  | Defines the type coupling on the inlet of the breeching inlet.
Type of hose reel |  | Identifies hosereel type.
Type of mounting |  | Defines how the luminaire is placed (surface mounted, recessed, etc.)
Type of placement |  | Indicates how the radiator is designed to be positioned.
Type of security lighting |  | Indicates the type of security lighting.
Type of sprinkler |  | Defines the type of sprinkler.
Type of storage |  | Defines the type of storage.
Ventilation gap surface | x | Indicates the opening area for air passage (ventilation).
Voltage |  | Defines the voltage that a device is designed to handle.
Wall covering thickness |  | Indicates the thickness of the wall finish material if it is not modelled separately.
Wall finishing |  | Indicates the wall finish material if not modelled separately.
Work package | x | Determines the batch in which this element is executed.
Documentation
Communication protocol |  | The communication protocol defines the communication methods used by the device to deliver the information.
Construction details |  | The execution details are detailed technical drawings enabling the correct installation of the element.
Construction principle |  | The construction principle is a note containing a text and/or summary diagrams defining the planned construction system. Example : type of structure, finishing and doors/windows, etc.
Energy report |  | The energy report includes an energy calculation of heat loss from the project and its technical equipment. Example : energy passport, EPB declaration, etc.
Environmental performance declaration |  | The environmental performance declaration is a document where the manufacturer declares the environmental impact of the product as defined by EN 15804.
Expansion joints plan |  | The expansion joint plan shows the location of the joints to allow proper expansion of an element.
Formwork plan |  | The formwork plan is a construction plan for a reinforced or prestressed concrete structure on which are shown all the dimensions defining the geometry of the structure.
Geotechnical study report |  | The geotechnical study report is a summary of the geotechnical tests carried out on site and the recommendations to be taken into account.
Installation instructions |  | The installation instructions contain the instructions for installing the technical component.
Layout plan |  | The layout plan indicates the assembly of the elements to create a coherent, aesthetically pleasing whole. Example : layout of tiling or metal cassettes on the facade.
List of doors |  | The door nomenclature is a table listing the doors and their features and equipment.
List of rooms |  | The list of rooms is a table listing the rooms and their characteristics. It is organised by zone.
Maintenance instructions |  | The maintenance instructions describes the instructions for servicing the technical equipment.
Maintenance log |  | The maintenance log is a document that lists the maintenance work carried out on the component: date, person involved, purpose.
Measurement protocol |  | The measurement protocol defines the calculation rules needed to use and calibrate the equipment.
Operating loads |  | The operating loads is a document which indicates the loads per part to which the element will be subjected.
Performances requirements |  | The performance to be achieved covers all the performance requirements that the element must meet. Example : thermal, fire, safety, etc.
Plan of openings |  | The plan of the openings shows the location of the openings to be created for the passage of ducts and other technical equipment.
Pre-calculation |  | The pre-calculation includes a note and possibly diagrams indicating, after simplified calculation, the dimensioning required for the element.
Precise calculation |  | The precise calculation includes a note and possibly diagrams indicating, after detailed calculation, the exact dimensioning required for the element. It concerns techniques.
Representative image |  | The representative image shows the element as envisaged. It shows the aesthetics, position and overall dimensions of the component. It can be found directly in the data sheet once the product has been chosen.
Shading principle |  | The shading principle is a note containing a text and/or diagram describing the system envisaged for obscuring the glazing.
Single-line diagram |  | The single-line diagram is presented in the form of a plan and shows the circuits of an electrical, sanitary or ventilation installation. It shows the connections and networks.
Space planning diagram |  | The space planning diagram is an organisation chart showing the spaces grouped by zone and the links between them.
Space requirement schema |  | The space requirement schema represents the space required to install the element and the space needed for its operation and maintenance. For example : the overall dimensions of escalator equipment, the dimensions of technical voids for the passage of ducts and pipes, the space required for suspended ceiling techniques, the space required to replace a part in a boiler.
Specific elements plan |  | The plan of the specific elements is a complementary document to the other required documents and is essential for a good understanding of the implementation of the element.
Specifications |  | The specifications set out all the requirements that the component must meet.
Stability report |  | The stability report includes the calculation note for the project's structural elements and the load description.
Steel reinforcement plan |  | The reinforcement plan shows the reinforcement to be used and its specific characteristics.
Technical recommendations |  | The technical recommendations set out the technical requirements that the component must meet.
Technical sheets |  | The technical sheet for a manufactured item lists its performance and technical characteristics. A representative image is attached to this document.
Zone data sheet |  | The zone sheet is a description of the zone, listing the common characteristics of the areas that make up the zone.

## IFC mapping
IFC mapping
GROUP | ELEMENT | IFC 2X3 TC1 | IFC 4 ADD2 | IFC 4.3
Actuator | Shutter/blind motor | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Door closer | IfcActuatorType.HANDOPERATEDACTUATOR | IfcActuator.HANDOPERATEDACTUATOR | IfcActuator.HANDOPERATEDACTUATOR
Actuator | Motorised door closer (door opener) | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Magnetic contact (door strike or holder) | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Motorised lock | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Mechanical lock | IfcActuatorType.HANDOPERATEDACTUATOR | IfcActuator.HANDOPERATEDACTUATOR | IfcActuator.HANDOPERATEDACTUATOR
Actuator | Compressed air motor smoke vent | IfcActuatorType.PNEUMATICACTUATOR | IfcActuator.PNEUMATICACTUATOR | IfcActuator.PNEUMATICACTUATOR
Actuator | Electric motor smoke outlet | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Magnetic lock | IfcActuatorType.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR | IfcActuator.ELECTRICACTUATOR
Actuator | Hydraulic mechanism (opening, support,etc.) | IfcActuatorType.HYDRAULICACTUATOR | IfcActuator.HYDRAULICACTUATOR | IfcActuator.HYDRAULICACTUATOR
Air handling unit | Air handling unit (ahu) | IfcUnitaryEquipmentType.AIRHANDLER | IfcUnitaryEquipment.AIRHANDLER | IfcUnitaryEquipment.AIRHANDLER
Air handling unit | Air-to-air heat pump (including reversible) | IfcUnitaryEquipmentType.SPLITSYSTEM | IfcUnitaryEquipment.SPLITSYSTEM | IfcUnitaryEquipment.SPLITSYSTEM
Air handling unit | Dehumidifier | IfcUnitaryEquipmentType.USERDEFINED[DEHUMIDIFIER] | IfcUnitaryEquipment.DEHUMIDIFIER | IfcUnitaryEquipment.DEHUMIDIFIER
Air-to-air exchanger | Counterflow plate heat exchanger | IfcAirToAirHeatRecoveryType.FIXEDPLATECOUNTERFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATECOUNTERFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATECOUNTERFLOWEXCHANGER
Air-to-air exchanger | Cross flow plate heat exchanger | IfcAirToAirHeatRecoveryType.FIXEDPLATECROSSFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATECROSSFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATECROSSFLOWEXCHANGER
Air-to-air exchanger | Parallel flow plate heat exchanger | IfcAirToAirHeatRecoveryType.FIXEDPLATEPARALLELFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATEPARALLELFLOWEXCHANGER | IfcAirToAirHeatRecovery.FIXEDPLATEPARALLELFLOWEXCHANGER
Air-to-air exchanger | Wheel heat exchanger | IfcAirToAirHeatRecoveryType.ROTARYWHEEL | IfcAirToAirHeatRecovery.ROTARYWHEEL | IfcAirToAirHeatRecovery.ROTARYWHEEL
Air-to-air exchanger | Tube heat exchanger | IfcAirToAirHeatRecoveryType.RUNAROUNDCOILLOOP | IfcAirToAirHeatRecovery.RUNAROUNDCOILLOOP | IfcAirToAirHeatRecovery.RUNAROUNDCOILLOOP
Air-to-air exchanger | Enthalpy exchanger | IfcAirToAirHeatRecoveryType.TWINTOWERENTHALPYRECOVERYLOOPS | IfcAirToAirHeatRecovery.TWINTOWERENTHALPYRECOVERYLOOPS | IfcAirToAirHeatRecovery.TWINTOWERENTHALPYRECOVERYLOOPS
Audiovisual device | Power amplifier | IfcElectricApplianceType.USERDEFINED[AMPLIFIER] | IfcAudioVisualAppliance.AMPLIFIER | IfcAudioVisualAppliance.AMPLIFIER
Audiovisual device | Integrated amplifier | IfcElectricApplianceType.USERDEFINED[AMPLIFIER] | IfcAudioVisualAppliance.AMPLIFIER | IfcAudioVisualAppliance.AMPLIFIER
Audiovisual device | Audio-video switch | IfcElectricApplianceType.USERDEFINED[SWITCHER] | IfcAudioVisualAppliance.SWITCHER | IfcAudioVisualAppliance.SWITCHER
Audiovisual device | Screen | IfcElectricApplianceType.TV | IfcAudioVisualAppliance.DISPLAY | IfcAudioVisualAppliance.DISPLAY
Audiovisual device | Speaker | IfcElectricApplianceType.USERDEFINED[SPEAKER] | IfcAudioVisualAppliance.SPEAKER | IfcAudioVisualAppliance.SPEAKER
Audiovisual device | Alarm speaker (fire/voice alarm) | IfcElectricApplianceType.USERDEFINED[SPEAKER] | IfcAudioVisualAppliance.SPEAKER | IfcAudioVisualAppliance.SPEAKER
Audiovisual device | Media player | IfcElectricApplianceType.USERDEFINED[PLAYER] | IfcAudioVisualAppliance.PLAYER | IfcAudioVisualAppliance.PLAYER
Audiovisual device | Television | IfcElectricApplianceType.TV | IfcAudioVisualAppliance.DISPLAY | IfcAudioVisualAppliance.DISPLAY
Audiovisual device | TV | IfcElectricApplianceType.TV | IfcAudioVisualAppliance.DISPLAY | IfcAudioVisualAppliance.DISPLAY
Audiovisual device | Camera | IfcElectricApplianceType.USERDEFINED[CAMERA] | IfcAudioVisualAppliance.CAMERA | IfcAudioVisualAppliance.CAMERA
Audiovisual device | Camera | IfcElectricApplianceType.USERDEFINED[CAMERA] | IfcAudioVisualAppliance.CAMERA | IfcAudioVisualAppliance.CAMERA
Audiovisual device | Camera ip | IfcElectricApplianceType.USERDEFINED[CAMERA] | IfcAudioVisualAppliance.CAMERA | IfcAudioVisualAppliance.CAMERA
Audiovisual device | Dome camera | IfcElectricApplianceType.USERDEFINED[CAMERA] | IfcAudioVisualAppliance.CAMERA | IfcAudioVisualAppliance.CAMERA
Audiovisual device | video conferencing camera | IfcElectricApplianceType.USERDEFINED[CAMERA] | IfcAudioVisualAppliance.CAMERA | IfcAudioVisualAppliance.CAMERA
Audiovisual device | Intercom | IfcElectricApplianceType.USERDEFINED[INTERCOM] | IfcAudioVisualAppliance.USERDEFINED[INTERCOM] | IfcAudioVisualAppliance.USERDEFINED[INTERCOM]
Audiovisual device | Video intercom | IfcElectricApplianceType.USERDEFINED[VIDEOINTERCOM] | IfcAudioVisualAppliance.USERDEFINED[VIDEOINTERCOM] | IfcAudioVisualAppliance.USERDEFINED[VIDEOINTERCOM]
Audiovisual device | Video decoder | IfcElectricApplianceType.USERDEFINED[TUNER] | IfcAudioVisualAppliance.TUNER | IfcAudioVisualAppliance.TUNER
Audiovisual device | TV box | IfcElectricApplianceType.USERDEFINED[TUNER] | IfcAudioVisualAppliance.TUNER | IfcAudioVisualAppliance.TUNER
Audiovisual device | Microphone | IfcElectricApplianceType.USERDEFINED[MICROPHONE] | IfcAudioVisualAppliance.MICROPHONE | IfcAudioVisualAppliance.MICROPHONE
Audiovisual device | Radio tuner | IfcElectricApplianceType.USERDEFINED[TUNER] | IfcAudioVisualAppliance.TUNER | IfcAudioVisualAppliance.TUNER
Audiovisual device | Projector | IfcElectricApplianceType.USERDEFINED[PROJECTOR] | IfcAudioVisualAppliance.PROJECTOR | IfcAudioVisualAppliance.PROJECTOR
Audiovisual device | Telephone | IfcElectricApplianceType.TELEPHONE | IfcAudioVisualAppliance.TELEPHONE | IfcAudioVisualAppliance.TELEPHONE
Beam | Metal girder | IfcBeam.BEAM | IfcBeam.BEAM | IfcBeam.BEAM
Beam | Ring beam | IfcBeam.USERDEFINED[RING_BEAM] | IfcBeam.USERDEFINED[RING_BEAM] | IfcBeam.USERDEFINED[RING_BEAM]
Beam | Floor support beam | IfcBeam.JOIST | IfcBeam.JOIST | IfcBeam.JOIST
Beam | Lintel | IfcBeam.LINTEL | IfcBeam.LINTEL | IfcBeam.LINTEL
Beam | Spandrel beam | IfcBeam.USERDEFINED[SPANDREL] | IfcBeam.SPANDREL | IfcBeam.SPANDREL
Beam | Inverted beam | IfcBeam.USERDEFINED[SPANDREL] | IfcBeam.SPANDREL | IfcBeam.SPANDREL
Beam | Castellated beam | IfcBeam.BEAM | IfcBeam.BEAM | IfcBeam.BEAM
Beam | Cellular beam | IfcBeam.BEAM | IfcBeam.BEAM | IfcBeam.BEAM
Breeching inlet | Breeching inlet | IfcFireSuppressionTerminalType.BREECHINGINLET | IfcFireSuppressionTerminal.BREECHINGINLET | IfcFireSuppressionTerminal.BREECHINGINLET
Cable tray | Cable tray | IfcCableCarrierSegmentType.CABLETRAYSEGMENT | IfcCableCarrierSegment.CABLETRAYSEGMENT | IfcCableCarrierSegment.CABLETRAYSEGMENT
Cable tray | Closed cable tray | IfcCableCarrierSegmentType.CABLETRUNKINGSEGMENT | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT
Cable tray | Cable ladder | IfcCableCarrierSegmentType.CABLELADDERSEGMENT | IfcCableCarrierSegment.CABLELADDERSEGMENT | IfcCableCarrierSegment.CABLELADDERSEGMENT
Cable tray | Electrical trunking | IfcCableCarrierSegmentType.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT
Cable tray | Technical channel | IfcCableCarrierSegmentType.CABLETRUNKINGSEGMENT | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT
Cable tray | Rigid protection tube (exposed cable) | IfcCableCarrierSegmentType.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT
Cable tray | Corrugated sheath | IfcCableCarrierSegmentType.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT | IfcCableCarrierSegment.CONDUITSEGMENT
Cable tray connection | 4-way crossing | IfcCableCarrierFittingType.CROSS | IfcCableCarrierFitting.CROSS | IfcCableCarrierFitting.JUNCTION
Cable tray connection | Corner fitting | IfcCableCarrierFittingType.BEND | IfcCableCarrierFitting.BEND | IfcCableCarrierFitting.BEND
Cable tray connection | T-fitting | IfcCableCarrierFittingType.TEE | IfcCableCarrierFitting.TEE | IfcCableCarrierFitting.JUNCTION
Cable tray connection | Reduction | IfcCableCarrierFittingType.REDUCER | IfcCableCarrierFitting.REDUCER | IfcCableCarrierFitting.TRANSITION
Caisson foundation | Caisson foundation | IfcFooting.USERDEFINED[CAISSON_FOUNDATION] | IfcFooting.CAISSON_FOUNDATION | IfcFooting.CAISSON_FOUNDATION
Ceiling finishing | Ceiling finishing | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Plasterboard | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Tiling | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Stone cladding (marble, granite,etc.) | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Cladding (metal, cassette, stone,etc.) | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Plaster (plaster, clay, lime, cement,etc.) | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Metal tray | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Sandwich panel | IfcCovering.CEILING | IfcCovering.CEILING | IfcCovering.CEILING
Ceiling finishing | Battens | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Ceiling finishing | Ceiling paint | IfcCovering.USERDEFINED[PAINTING] | IfcCovering.USERDEFINED[CEILING_PAINTING] | IfcCovering.USERDEFINED[PAINTING]
Chiller | Air conditioner | IfcChillerType.AIRCOOLED | IfcChiller.AIRCOOLED | IfcChiller.AIRCOOLED
Chimney | Whole chimney | IfcBuildingElementProxy.USERDEFINED[CHIMNEY] | IfcChimney.NOTDEFINED | IfcChimney.NOTDEFINED
Column | Column (isolated) | IfcColumn.COLUMN | IfcColumn.COLUMN | IfcColumn.COLUMN
Column | Pilaster (wall) | IfcColumn.USERDEFINED[PILASTER] | IfcColumn.PILASTER | IfcColumn.PILASTER
Curtain wall | Curtain wall | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED
Curtain wall | Canopy | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED
Curtain wall | Veranda | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED | IfcCurtainWall.NOTDEFINED
Damper and register | Hood | IfcDamperType.FUMEHOODEXHAUST | IfcDamper.FUMEHOODEXHAUST | IfcDamper.FUMEHOODEXHAUST
Damper and register | Backdraft damper | IfcDamperType.BACKDRAFTDAMPER | IfcDamper.BACKDRAFTDAMPER | IfcDamper.BACKDRAFTDAMPER
Damper and register | Fire damper | IfcDamperType.FIREDAMPER | IfcDamper.FIREDAMPER | IfcDamper.FIREDAMPER
Damper and register | Smoke damper (chimney) | IfcDamperType.SMOKEDAMPER | IfcDamper.SMOKEDAMPER | IfcDamper.SMOKEDAMPER
Damper and register | Smoke damper (fire) | IfcDamperType.FIRESMOKEDAMPER | IfcDamper.FIRESMOKEDAMPER | IfcDamper.FIRESMOKEDAMPER
Damper and register | Balancing damper | IfcDamperType.BALANCINGDAMPER | IfcDamper.BALANCINGDAMPER | IfcDamper.BALANCINGDAMPER
Damper and register | Motorised damper | IfcDamperType.CONTROLDAMPER | IfcDamper.CONTROLDAMPER | IfcDamper.CONTROLDAMPER
Damper and register | Blast damper | IfcDamperType.BLASTDAMPER | IfcDamper.BLASTDAMPER | IfcDamper.BLASTDAMPER
Damper and register | Pressure relief damper | IfcDamperType.RELIEFDAMPER | IfcDamper.RELIEFDAMPER | IfcDamper.RELIEFDAMPER
Damper and register | Vacuum damper | IfcDamperType.RELIEFDAMPER | IfcDamper.RELIEFDAMPER | IfcDamper.RELIEFDAMPER
Data device | Mobile phone antenna | IfcElectricApplianceType.USERDEFINED[ANTENNA] | IfcCommunicationsAppliance.ANTENNA | IfcCommunicationsAppliance.ANTENNA
Data device | Mobile phone relay | IfcElectricApplianceType.USERDEFINED[ANTENNA] | IfcCommunicationsAppliance.ANTENNA | IfcCommunicationsAppliance.ANTENNA
Data device | Home automation gateway | IfcElectricApplianceType.USERDEFINED[GATEWAY] | IfcCommunicationsAppliance.GATEWAY | IfcCommunicationsAppliance.GATEWAY
Data device | Antenna | IfcElectricApplianceType.USERDEFINED[ANTENNA] | IfcCommunicationsAppliance.ANTENNA | IfcCommunicationsAppliance.ANTENNA
Data device | Printer | IfcElectricApplianceType.PRINTER | IfcCommunicationsAppliance.PRINTER | IfcCommunicationsAppliance.PRINTER
Data device | Computer | IfcElectricApplianceType.COMPUTER | IfcCommunicationsAppliance.COMPUTER | IfcCommunicationsAppliance.COMPUTER
Data device | Server | IfcElectricApplianceType.COMPUTER | IfcCommunicationsAppliance.COMPUTER | IfcCommunicationsAppliance.COMPUTER
Data device | Network hub | IfcElectricApplianceType.USERDEFINED[NETWORKHUB] | IfcCommunicationsAppliance.NETWORKHUB | IfcCommunicationsAppliance.NETWORKHUB
Data device | Data switch | IfcElectricApplianceType.USERDEFINED[NETWORKHUB] | IfcCommunicationsAppliance.NETWORKHUB | IfcCommunicationsAppliance.NETWORKHUB
Data device | Fax | IfcElectricApplianceType.USERDEFINED[FAX] | IfcCommunicationsAppliance.FAX | IfcCommunicationsAppliance.FAX
Data device | Internet modem | IfcElectricApplianceType.USERDEFINED[MODEM] | IfcCommunicationsAppliance.MODEM | IfcCommunicationsAppliance.MODEM
Data device | Network accessory (firewall, network load balancer,etc.) | IfcElectricApplianceType.USERDEFINED[NETWORKAPPLIANCE] | IfcCommunicationsAppliance.NETWORKAPPLIANCE | IfcCommunicationsAppliance.NETWORKAPPLIANCE
Data device | Repeater (Wifi, gsm,etc.) | IfcElectricApplianceType.USERDEFINED[REPEATER] | IfcCommunicationsAppliance.REPEATER | IfcCommunicationsAppliance.REPEATER
Data device | Scanner | IfcElectricApplianceType.SCANNER | IfcCommunicationsAppliance.SCANNER | IfcCommunicationsAppliance.SCANNER
Data device | Router (wifi access point,etc.) | IfcElectricApplianceType.USERDEFINED[ROUTER] | IfcCommunicationsAppliance.ROUTER | IfcCommunicationsAppliance.ROUTER
Deep foundation | False wells | IfcPile.SUPPORT | IfcPile.SUPPORT | IfcPile.SUPPORT
Deep foundation | Driven pile | IfcPile.USERDEFINED[DRIVEN] | IfcPile.DRIVEN | IfcPile.DRIVEN
Deep foundation | Bored pile | IfcPile.USERDEFINED[BORED] | IfcPile.BORED | IfcPile.BORED
Deep foundation | Jet grouting pile | IfcPile.USERDEFINED[JETGROUTING] | IfcPile.JETGROUTING | IfcPile.JETGROUTING
Deep foundation | Vibrated pile | IfcPile.USERDEFINED[DRIVEN] | IfcPile.DRIVEN | IfcPile.DRIVEN
Deep foundation | MV pile | IfcPile.USERDEFINED[DRIVEN] | IfcPile.DRIVEN | IfcPile.DRIVEN
Deep foundation | CFA pile | IfcPile.USERDEFINED[BORED] | IfcPile.BORED | IfcPile.BORED
Deep foundation | Screw pile | IfcPile.USERDEFINED[SCREW_PILE] | IfcPile.USERDEFINED[SCREW_PILE] | IfcPile.USERDEFINED[SCREW_PILE]
Deep foundation | Pipe pile | IfcPile.USERDEFINED[DRIVEN] | IfcPile.DRIVEN | IfcPile.DRIVEN
Deep foundation | Soil mix | IfcPile.USERDEFINED[SOILMIX] | IfcPile.USERDEFINED[SOILMIX] | IfcPile.USERDEFINED[SOILMIX]
Deep foundation | Micropile | IfcPile.USERDEFINED[BORED] | IfcPile.BORED | IfcPile.BORED
Deep foundation | Stone columns | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS]
Deep foundation | Rigid inclusions | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS]
Door | Door | IfcDoor | IfcDoor | IfcDoor
Door | Gate | IfcDoor | IfcDoor.GATE | IfcDoor.GATE
Door | Wicket gate | IfcDoor | IfcDoor.GATE | IfcDoor.GATE
Door | Inspection hatch | IfcDoor | IfcDoor.TRAPDOOR | IfcDoor.TRAPDOOR
Door | Access hatch | IfcDoor | IfcDoor.TRAPDOOR | IfcDoor.TRAPDOOR
Door | Garage door | IfcDoor | IfcDoor.DOOR | IfcDoor.DOOR
Door | Arm barrier | IfcDoor | IfcDoor.GATE | IfcDoor.GATE
Electric appliance | Freezer | IfcElectricApplianceType.FREEZER | IfcElectricAppliance.FREEZER | IfcElectricAppliance.FREEZER
Electric appliance | Combined refrigerator | IfcElectricApplianceType.FRIDGE_FREEZER | IfcElectricAppliance.FRIDGE_FREEZER | IfcElectricAppliance.FRIDGE_FREEZER
Electric appliance | Fridge | IfcElectricApplianceType.REFRIGERATOR | IfcElectricAppliance.REFRIGERATOR | IfcElectricAppliance.REFRIGERATOR
Electric appliance | Refrigerator | IfcElectricApplianceType.REFRIGERATOR | IfcElectricAppliance.REFRIGERATOR | IfcElectricAppliance.REFRIGERATOR
Electric appliance | Dishwasher | IfcElectricApplianceType.DISHWASHER | IfcElectricAppliance.DISHWASHER | IfcElectricAppliance.DISHWASHER
Electric appliance | Microwave | IfcElectricApplianceType.MICROWAVE | IfcElectricAppliance.MICROWAVE | IfcElectricAppliance.MICROWAVE
Electric appliance | Photocopier | IfcElectricApplianceType.PHOTOCOPIER | IfcElectricAppliance.PHOTOCOPIER | IfcElectricAppliance.PHOTOCOPIER
Electric appliance | Hob | IfcElectricApplianceType.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER
Electric appliance | Cooking hob | IfcElectricApplianceType.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER
Electric appliance | Electric cooker | IfcElectricApplianceType.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER | IfcElectricAppliance.ELECTRICCOOKER
Electric appliance | Kitchen robot | IfcElectricApplianceType.USERDEFINED[KITCHENMACHINE] | IfcElectricAppliance.KITCHENMACHINE | IfcElectricAppliance.KITCHENMACHINE
Electric appliance | Kitchen machine | IfcElectricApplianceType.USERDEFINED[KITCHENMACHINE] | IfcElectricAppliance.KITCHENMACHINE | IfcElectricAppliance.KITCHENMACHINE
Electric appliance | Fixed hair dryer | IfcElectricApplianceType.USERDEFINED[HAIRDRYER] | IfcElectricAppliance.USERDEFINED[HAIRDRYER] | IfcElectricAppliance.USERDEFINED[HAIRDRYER]
Electric appliance | Hand dryer | IfcElectricApplianceType.HANDDRYER | IfcElectricAppliance.HANDDRYER | IfcElectricAppliance.HANDDRYER
Electric appliance | Oven | IfcElectricApplianceType.USERDEFINED[OVEN] | IfcElectricAppliance.USERDEFINED[OVEN] | IfcElectricAppliance.USERDEFINED[OVEN]
Electric appliance | Washing machine | IfcElectricApplianceType.WASHINGMACHINE | IfcElectricAppliance.WASHINGMACHINE | IfcElectricAppliance.WASHINGMACHINE
Electric appliance | Tumble dryer | IfcElectricApplianceType.TUMBLEDRYER | IfcElectricAppliance.TUMBLEDRYER | IfcElectricAppliance.TUMBLEDRYER
Electric appliance | Cash dispenser | IfcElectricApplianceType.USERDEFINED[ATM] | IfcElectricAppliance.USERDEFINED[ATM] | IfcElectricAppliance.USERDEFINED[ATM]
Electric appliance | ATM | IfcElectricApplianceType.USERDEFINED[ATM] | IfcElectricAppliance.USERDEFINED[ATM] | IfcElectricAppliance.USERDEFINED[ATM]
Electric appliance | Water cooler | IfcElectricApplianceType.WATERCOOLER | IfcElectricAppliance.FREESTANDINGWATERCOOLER | IfcElectricAppliance.FREESTANDINGWATERCOOLER
Electrical generator | Cogenerator | IfcElectricGeneratorType.USERDEFINED[CHP] | IfcElectricGenerator.CHP | IfcElectricGenerator.CHP
Electrical generator | Generator set | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | IfcElectricGenerator.ENGINEGENERATOR | IfcElectricGenerator.ENGINEGENERATOR
Electrical generator | Safety electric generator | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | IfcElectricGenerator.ENGINEGENERATOR | IfcElectricGenerator.ENGINEGENERATOR
Electrical generator | Replacement generator set (operation) | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | IfcElectricGenerator.ENGINEGENERATOR | IfcElectricGenerator.ENGINEGENERATOR
Electrical generator | Production generator set | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | IfcElectricGenerator.ENGINEGENERATOR | IfcElectricGenerator.ENGINEGENERATOR
Electrical generator | Electric generator (without combustion engine) | IfcElectricGeneratorType.USERDEFINED[STANDALONE] | IfcElectricGenerator.STANDALONE | IfcElectricGenerator.STANDALONE
Electrical outlet | Electrical outlet (single-phase, three-phase .,etc.) | IfcOutletType.POWEROUTLET | IfcOutlet.POWEROUTLET | IfcOutlet.POWEROUTLET
Electrical outlet | Data socket (RJ45,etc.) | IfcOutletType.USERDEFINED[DATAOUTLET] | IfcOutlet.DATAOUTLET | IfcOutlet.DATAOUTLET
Electrical outlet | Telephone socket (RJ11,etc.) | IfcOutletType.USERDEFINED[TELEPHONEOUTLET] | IfcOutlet.TELEPHONEOUTLET | IfcOutlet.TELEPHONEOUTLET
Electrical outlet | Audiovisual socket (RCA, mini-jack, jack, XlR, mini-DIN, VGA SubD15, DVI, HDMI, DP, coaxial antenna and TV,etc.) | IfcOutletType.AUDIOVISUALOUTLET | IfcOutlet.AUDIOVISUALOUTLET | IfcOutlet.AUDIOVISUALOUTLET
Electrical outlet | Car charging station | IfcOutletType.USERDEFINED[CHARGING_STATION] | IfcOutlet.USERDEFINED[CHARGING_STATION] | IfcOutlet.USERDEFINED[CHARGING_STATION]
Electrical panel | Electric consumer unit | IfcElectricDistributionPoint | IfcElectricDistributionBoard.CONSUMERUNIT | IfcElectricDistributionBoard.CONSUMERUNIT
Electrical panel | Electric switchboard | IfcElectricDistributionPoint | IfcElectricDistributionBoard.SWITCHBOARD | IfcElectricDistributionBoard.SWITCHBOARD
Electrical panel | Electric distribution board | IfcElectricDistributionPoint | IfcElectricDistributionBoard.DISTRIBUTIONBOARD | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Electrical panel | Main low voltage distribution board | IfcElectricDistributionPoint | IfcElectricDistributionBoard.DISTRIBUTIONBOARD | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Electrical panel | Temporary electrical panel | IfcElectricDistributionPoint | IfcElectricDistributionBoard.DISTRIBUTIONBOARD | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Electrical panel | Data board | IfcElectricDistributionPoint | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Electrical panel | Data rack | IfcElectricDistributionPoint | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Electrical panel | Server rack | IfcElectricDistributionPoint | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Electrical panel | Server cabinet | IfcElectricDistributionPoint | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Electrical panel | Wiring closet | IfcElectricDistributionPoint | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Electrical protection equipment | Fuse | IfcProtectiveDeviceType.FUSEDISCONNECTOR | IfcProtectiveDevice.FUSEDISCONNECTOR | IfcProtectiveDevice.FUSEDISCONNECTOR
Electrical protection equipment | Main circuit breaker | IfcProtectiveDeviceType.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER
Electrical protection equipment | Circuit breaker | IfcProtectiveDeviceType.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER
Electrical protection equipment | Disconnecting switch | IfcProtectiveDeviceType.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER | IfcProtectiveDevice.CIRCUITBREAKER
Electrical protection equipment | Differential circuit breaker | IfcProtectiveDeviceType.RESIDUALCURRENTCIRCUITBREAKER | IfcProtectiveDevice.RESIDUALCURRENTCIRCUITBREAKER | IfcProtectiveDevice.RESIDUALCURRENTCIRCUITBREAKER
Electrical protection equipment | Earth leakage circuit breaker | IfcProtectiveDeviceType.USERDEFINED[EARTHLEAKAGECIRCUITBREAKER] | IfcProtectiveDevice.EARTHLEAKAGECIRCUITBREAKER | IfcProtectiveDevice.EARTHLEAKAGECIRCUITBREAKER
Electrical protection equipment | Earthing switch | IfcProtectiveDeviceType.USERDEFINED[EARTHINGSWITCH] | IfcProtectiveDevice.EARTHINGSWITCH | IfcProtectiveDevice.EARTHINGSWITCH
Electrical protection equipment | Surge protector | IfcProtectiveDeviceType.VARISTOR | IfcProtectiveDevice.VARISTOR | IfcProtectiveDevice.VARISTOR
Electrical switch | Single pole switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Single-pole two-way switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Single-pole pull switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Double-pole switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Two-Pole Two-Way Switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Three-pole switch | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Changeover switch | IfcSwitchingDeviceType.TOGGLESWITCH | IfcSwitchingDevice.TOGGLESWITCH | IfcSwitchingDevice.TOGGLESWITCH
Electrical switch | Timer | IfcSwitchingDeviceType.USERDEFINED[TIMER] | IfcSwitchingDevice.USERDEFINED[TIMER] | IfcSwitchingDevice.USERDEFINED[TIMER]
Electrical switch | Push button | IfcSwitchingDeviceType.CONTACTOR | IfcSwitchingDevice.CONTACTOR | IfcSwitchingDevice.CONTACTOR
Electrical switch | Pulse switch (door closing) | IfcSwitchingDeviceType.STARTER | IfcSwitchingDevice.STARTER | IfcSwitchingDevice.STARTER
Electrical switch | Inverter | IfcSwitchingDeviceType.USERDEFINED[DIMMER_SWITCH] | IfcSwitchingDevice.DIMMERSWITCH | IfcSwitchingDevice.DIMMERSWITCH
Electrical switch | Dimmer switch | IfcSwitchingDeviceType.USERDEFINED[DIMMER_SWITCH] | IfcSwitchingDevice.DIMMERSWITCH | IfcSwitchingDevice.DIMMERSWITCH
Electrical switch | Patient call button | IfcSwitchingDeviceType.STARTER | IfcSwitchingDevice.STARTER | IfcSwitchingDevice.STARTER
Electrical switch | Foot switch for switching control | IfcSwitchingDeviceType.TOGGLESWITCH | IfcSwitchingDevice.TOGGLESWITCH | IfcSwitchingDevice.TOGGLESWITCH
Electrical switch | AV system port switch | IfcSwitchingDeviceType.USERDEFINED[SELECTORSWITCH] | IfcSwitchingDevice.SELECTORSWITCH | IfcSwitchingDevice.SELECTORSWITCH
Electrical transformer | Voltage transformer | IfcTransformerType.VOLTAGE | IfcTransformer.VOLTAGE | IfcTransformer.VOLTAGE
Electrical transformer | Isolation transformer | IfcTransformerType.USERDEFINED[ISOLATIONTRANSFORMER] | IfcTransformer.USERDEFINED[ISOLATIONTRANSFORMER] | IfcTransformer.USERDEFINED[ISOLATIONTRANSFORMER]
Electrical transformer | Measuring transformer | IfcTransformerType.CURRENT | IfcTransformer.CURRENT | IfcTransformer.CURRENT
Electrical transformer | Inverter transformer | IfcTransformerType.USERDEFINED[INVERTER] | IfcTransformer.INVERTER | IfcTransformer.INVERTER
Electrical transformer | Inverter | IfcTransformerType.USERDEFINED[INVERTER] | IfcTransformer.INVERTER | IfcTransformer.INVERTER
Electrical transformer | Transformer rectifier | IfcTransformerType.USERDEFINED[RECTIFIER] | IfcTransformer.RECTIFIER | IfcTransformer.RECTIFIER
Electrical transformer | Frequency inverter for motors | IfcTransformerType.FREQUENCY | IfcTransformer.FREQUENCY | IfcTransformer.FREQUENCY
Electricity storage | Battery (chemical storage) | IfcElectricFlowStorageDeviceType.BATTERY | IfcElectricFlowStorageDevice.BATTERY | IfcElectricFlowStorageDevice.BATTERY
Electricity storage | Capacitor bank | IfcElectricFlowStorageDeviceType.CAPACITORBANK | IfcElectricFlowStorageDevice.CAPACITORBANK | IfcElectricFlowStorageDevice.CAPACITORBANK
Electricity storage | Compensation battery | IfcElectricFlowStorageDeviceType.CAPACITORBANK | IfcElectricFlowStorageDevice.CAPACITORBANK | IfcElectricFlowStorageDevice.CAPACITORBANK
Electricity storage | Anti-harmonic | IfcElectricFlowStorageDeviceType.HARMONICFILTER | IfcElectricFlowStorageDevice.HARMONICFILTER | IfcElectricFlowStorageDevice.HARMONICFILTER
Electricity storage | Compensation inductor | IfcElectricFlowStorageDeviceType.INDUCTORBANK | IfcElectricFlowStorageDevice.INDUCTORBANK | IfcElectricFlowStorageDevice.INDUCTORBANK
Electricity storage | UPS/no-break | IfcElectricFlowStorageDeviceType.UPS | IfcElectricFlowStorageDevice.UPS | IfcElectricFlowStorageDevice.UPS
Extinguisher | ﻿ | IfcFlowTerminal - [IfcFireSuppressionTerminalType] IfcFireSuppressionTerminalTypeEnum | IfcFireSuppressionTerminal - IfcFireSuppressionTerminalTypeEnum
False ceiling | False ceiling | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
False ceiling | Suspended ceiling | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
False ceiling | Vertical ceiling closing | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
False ceiling | Technical ceiling | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
False ceiling | Battens | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Fan | Fan | IfcFanType | IfcFan | IfcFan
Filter | Air filter (G4, F7,etc.) | IfcFilterType.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER
Filter | HEPA filter | IfcFilterType.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER
Filter | Electrostatic filter | IfcFilterType.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER
Filter | Oil filter | IfcFilterType.OILFILTER | IfcFilter.OILFILTER | IfcFilter.OILFILTER
Filter | Cyclone filter | IfcFilterType.WATERFILTER | IfcFilter.WATERFILTER | IfcFilter.WATERFILTER
Filter | Water filter | IfcFilterType.WATERFILTER | IfcFilter.WATERFILTER | IfcFilter.WATERFILTER
Filter | Active carbon filter (water and air) | IfcFilterType.ODORFILTER | IfcFilter.ODORFILTER | IfcFilter.ODORFILTER
Filter | UV lamp (water treatment) | IfcFilterType.WATERFILTER | IfcFilter.WATERFILTER | IfcFilter.WATERFILTER
Filter | UV lamp (air treatment) | IfcFilterType.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER | IfcFilter.AIRPARTICLEFILTER
Fire hose reel | Fire hose reel | IfcFireSuppressionTerminalType.HOSEREEL | IfcFireSuppressionTerminal.HOSEREEL | IfcFireSuppressionTerminal.HOSEREEL
Fire hose reel | Fire hose | IfcFireSuppressionTerminalType.HOSEREEL | IfcFireSuppressionTerminal.HOSEREEL | IfcFireSuppressionTerminal.HOSEREEL
Fire hydrant | Fire hydrant | IfcFireSuppressionTerminalType.FIREHYDRANT | IfcFireSuppressionTerminal.FIREHYDRANT | IfcFireSuppressionTerminal.FIREHYDRANT
Fire protection cabinet | Fire protection cabinet | IfcFireSuppressionTerminalType.USERDEFINED[FIRE_CABINETS] | IfcFireSuppressionTerminal.USERDEFINED[FIRE_CABINETS] | IfcFireSuppressionTerminal.USERDEFINED[FIRE_CABINETS]
Floor finishing | Raised tiling | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Linoleum | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Stone covering | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Wooden decking | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Wooden floor | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Parquet flooring | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Tiling | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Carpet | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Floor panel | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Mortar screed | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Dry screed | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Filling screed | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Levelling screed | IfcCovering.FLOORING | IfcCovering.FLOORING | IfcCovering.FLOORING
Floor finishing | Sandwich panel | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Floor finishing | Battens | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Floor finishing | Floor paint | IfcCovering.USERDEFINED[PAINTING] | IfcCovering.USERDEFINED[FLOOR_PAINTING] | IfcCovering.USERDEFINED[PAINTING]
Foundation beam | Foundation beam | IfcFooting.FOOTING_BEAM | IfcFooting.FOOTING_BEAM | IfcFooting.FOOTING_BEAM
Foundation footing | Pad footing | IfcFooting.PAD_FOOTING | IfcFooting.PAD_FOOTING | IfcFooting.PAD_FOOTING
Foundation footing | Extra thickness slab (pad) | IfcFooting.PAD_FOOTING | IfcFooting.PAD_FOOTING | IfcFooting.PAD_FOOTING
Foundation footing | Strip footing | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING
Foundation footing | Wall footing | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING
Foundation footing | Extra thickness slab (strip) | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING | IfcFooting.STRIP_FOOTING
Furniture | Chair | IfcFurnishingElement | IfcFurniture.CHAIR | IfcFurniture.CHAIR
Furniture | Table | IfcFurnishingElement | IfcFurniture.TABLE | IfcFurniture.TABLE
Furniture | Desk | IfcFurnishingElement | IfcFurniture.DESK | IfcFurniture.DESK
Furniture | Cabinet | IfcFurnishingElement | IfcFurniture.FILECABINET | IfcFurniture.FILECABINET
Furniture | Kitchen furniture | IfcFurnishingElement | IfcFurniture.USERDEFINED[KITCHENFURNITURE] | IfcFurniture.USERDEFINED[KITCHENFURNITURE]
Furniture | Shelf | IfcFurnishingElement | IfcFurniture.SHELF | IfcFurniture.SHELF
Furniture | Sofa | IfcFurnishingElement | IfcFurniture.SOFA | IfcFurniture.SOFA
Furniture | Armchair | IfcFurnishingElement | IfcFurniture.CHAIR | IfcFurniture.CHAIR
Furniture | Bed | IfcFurnishingElement | IfcFurniture.BED | IfcFurniture.BED
Furniture | Planter | IfcFurnishingElement | IfcFurniture.USERDEFINED[PLANTER] | IfcFurniture.USERDEFINED[PLANTER]
Heat diffusion - radiator | Finned radiator | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | IfcSpaceHeater.RADIATOR | IfcSpaceHeater.RADIATOR
Heat diffusion - radiator | Electric radiator | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | IfcSpaceHeater.RADIATOR | IfcSpaceHeater.RADIATOR
Heat diffusion - radiator | Plate radiator | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | IfcSpaceHeater.RADIATOR | IfcSpaceHeater.RADIATOR
Heat diffusion - radiator | Towel dryer | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | IfcSpaceHeater.RADIATOR | IfcSpaceHeater.RADIATOR
Heat production - steam | Boiler | IfcBoilerType.STEAM | IfcBoiler.STEAM | IfcBoiler.STEAM
Heat production - water | Thermodynamic balloon | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Water heater | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Hot water tank | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Oil boiler | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Gas boiler | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Air-water heat pump (including reversible) | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Ground-water heat pump (including reversible) | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Wood boiler | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat production - water | Pellet boiler | IfcBoilerType.WATER | IfcBoiler.WATER | IfcBoiler.WATER
Heat/cold diffusion - surface | Radiant floor heating | IfcCoilType.WATERHEATINGCOIL | IfcCoil.WATERHEATINGCOIL | IfcCoil.WATERHEATINGCOIL
Heat/cold diffusion - surface | Radiant floor cooling | IfcCoilType.WATERCOOLINGCOIL | IfcCoil.WATERCOOLINGCOIL | IfcCoil.WATERCOOLINGCOIL
Heat/cold diffusion - surface | Radiant floor heating/cooling | IfcCoilType.HYDRONICCOIL | IfcCoil.HYDRONICCOIL | IfcCoil.HYDRONICCOIL
Heat/cold diffusion - surface | Direct expansion floor heating | IfcCoilType.DXCOOLINGCOIL | IfcCoil.DXCOOLINGCOIL | IfcCoil.DXCOOLINGCOIL
Heat/cold diffusion - surface | Active heating ceiling (water) | IfcCoilType.WATERHEATINGCOIL | IfcCoil.WATERHEATINGCOIL | IfcCoil.WATERHEATINGCOIL
Heat/cold diffusion - surface | Active cooling ceiling (water) | IfcCoilType.WATERCOOLINGCOIL | IfcCoil.WATERCOOLINGCOIL | IfcCoil.WATERCOOLINGCOIL
Heat/cold diffusion - surface | Active cooling/heating ceiling (water) | IfcCoilType.HYDRONICCOIL | IfcCoil.HYDRONICCOIL | IfcCoil.HYDRONICCOIL
Heat/cold diffusion - surface | Electric radiant ceiling | IfcCoilType.ELECTRICHEATINGCOIL | IfcCoil.ELECTRICHEATINGCOIL | IfcCoil.ELECTRICHEATINGCOIL
Heat/cold diffusion - surface | Electric radiant floor | IfcCoilType.ELECTRICHEATINGCOIL | IfcCoil.ELECTRICHEATINGCOIL | IfcCoil.ELECTRICHEATINGCOIL
Heat/cold distribution - convector | Baseboard heaters | IfcSpaceHeaterType.CONVECTOR | IfcSpaceHeater.CONVECTOR | IfcSpaceHeater.CONVECTOR
Heat/cold distribution - convector | Finned tubes | IfcSpaceHeaterType.CONVECTOR | IfcSpaceHeater.CONVECTOR | IfcSpaceHeater.CONVECTOR
Heat/cold distribution - convector | Fan coil unit | IfcSpaceHeaterType.CONVECTOR | IfcSpaceHeater.CONVECTOR | IfcSpaceHeater.CONVECTOR
Lift | Lift | IfcTransportElement.ELEVATOR | IfcTransportElement.ELEVATOR | IfcTransportElement.ELEVATOR
Lightfixture | Beam lighting | IfcLightFixtureType.POINTSOURCE | IfcLightFixture.POINTSOURCE | IfcLightFixture.POINTSOURCE
Lightfixture | Multidirectional lighting | IfcLightFixtureType.DIRECTIONSOURCE | IfcLightFixture.DIRECTIONSOURCE | IfcLightFixture.DIRECTIONSOURCE
Linear structural member | Floor joist | IfcMember.USERDEFINED[JOIST] | IfcMember.USERDEFINED[JOIST] | IfcMember.USERDEFINED[JOIST]
Linear structural member | Vertical timber frame element | IfcMember.STUD | IfcMember.STUD | IfcMember.STUD
Linear structural member | Horizontal beam timber frame | IfcMember.PLATE | IfcMember.PLATE | IfcMember.PLATE
Linear structural member | Rafter | IfcMember.RAFTER | IfcMember.RAFTER | IfcMember.RAFTER
Linear structural member | Bracing | IfcMember.BRACE | IfcMember.BRACE | IfcMember.BRACE
Linear structural member | Stringer | IfcMember.STRINGER | IfcMember.STRINGER | IfcMember.STRINGER
Linear structural member | Mullion | IfcMember.MULLION | IfcMember.MULLION | IfcMember.MULLION
Linear structural member | Curtain wall mullion | IfcMember.MULLION | IfcMember.MULLION | IfcMember.MULLION
Linear structural member | Purlin | IfcMember.PURLIN | IfcMember.PURLIN | IfcMember.PURLIN
Linear structural member | Chord | IfcMember.CHORD | IfcMember.CHORD | IfcMember.CHORD
Linear structural member | Wall plate | IfcMember.PURLIN | IfcMember.PURLIN | IfcMember.PURLIN
Linear structural member | Battens | IfcMember.RAFTER | IfcMember.RAFTER | IfcMember.RAFTER
Linear structural member | Hip rafter | IfcMember.RAFTER | IfcMember.RAFTER | IfcMember.RAFTER
Linear structural member | Ridge beam | IfcMember.PURLIN | IfcMember.PURLIN | IfcMember.PURLIN
Linear structural member | Top chord | IfcMember.CHORD | IfcMember.CHORD | IfcMember.CHORD
Linear structural member | Collar tie | IfcMember.COLLAR | IfcMember.COLLAR | IfcMember.COLLAR
Linear structural member | King post | IfcMember.POST | IfcMember.POST | IfcMember.POST
Linear structural member | Strut | IfcMember.STRUT | IfcMember.STRUT | IfcMember.STRUT
Management panel | Management panel | IfcDistributionControlElement | IfcUnitaryControlElement.CONTROLPANEL | IfcUnitaryControlElement.CONTROLPANEL
Management panel | Fire alarm control panel | IfcDistributionControlElement | IfcUnitaryControlElement.ALARMPANEL | IfcUnitaryControlElement.ALARMPANEL
Management panel | Alarm control panel | IfcDistributionControlElement | IfcUnitaryControlElement.ALARMPANEL | IfcUnitaryControlElement.ALARMPANEL
Pump | Generic pump | IfcPumpType.USERDEFINED[GENERIC] | IfcPump.USERDEFINED[GENERIC] | IfcPump.USERDEFINED[GENERIC]
Pump | Circulator | IfcPumpType.CIRCULATOR | IfcPump.CIRCULATOR | IfcPump.CIRCULATOR
Pump | Oil pump | IfcPumpType.USERDEFINED[OILPUMP] | IfcPump.USERDEFINED[OILPUMP] | IfcPump.USERDEFINED[OILPUMP]
Pump | Lift pump | IfcPumpType.USERDEFINED[SUMP_PITS] | IfcPump.USERDEFINED[SUMP_PITS] | IfcPump.USERDEFINED[SUMP_PITS]
Pump | Booster pump | IfcPumpType.USERDEFINED[WATERBOOSTER] | IfcPump.USERDEFINED[WATERBOOSTER] | IfcPump.USERDEFINED[WATERBOOSTER]
Pump | Water pump | IfcPumpType.USERDEFINED[WATERSUPPLY] | IfcPump.USERDEFINED[WATERSUPPLY] | IfcPump.USERDEFINED[WATERSUPPLY]
Pump | Fire pump | IfcPumpType.USERDEFINED[FIREPROTECTION] | IfcPump.USERDEFINED[FIREPROTECTION] | IfcPump.USERDEFINED[FIREPROTECTION]
Ramp | Straight run ramp | IfcRamp.STRAIGHT_RUN_RAMP | IfcRamp.STRAIGHT_RUN_RAMP | IfcRamp.STRAIGHT_RUN_RAMP
Ramp | Two straight run ramp | IfcRamp.TWO_STRAIGHT_RUN_RAMP | IfcRamp.TWO_STRAIGHT_RUN_RAMP | IfcRamp.TWO_STRAIGHT_RUN_RAMP
Ramp | Quarter turn ramp | IfcRamp.QUARTER_TURN_RAMP | IfcRamp.QUARTER_TURN_RAMP | IfcRamp.QUARTER_TURN_RAMP
Ramp | Two quarter turn ramp | IfcRamp.TWO_QUARTER_TURN_RAMP | IfcRamp.TWO_QUARTER_TURN_RAMP | IfcRamp.TWO_QUARTER_TURN_RAMP
Ramp | Half turn ramp | IfcRamp.HALF_TURN_RAMP | IfcRamp.HALF_TURN_RAMP | IfcRamp.HALF_TURN_RAMP
Ramp | Spiral ramp | IfcRamp.SPIRAL_RAMP | IfcRamp.SPIRAL_RAMP | IfcRamp.SPIRAL_RAMP
Ramp | Sloping ramp | IfcRamp.STRAIGHT_RUN_RAMP | IfcRamp.STRAIGHT_RUN_RAMP | IfcRamp.STRAIGHT_RUN_RAMP
Roof | Flat roof | IfcRoof.FLAT_ROOF | IfcRoof.FLAT_ROOF | IfcRoof.FLAT_ROOF
Roof | Shed roof | IfcRoof.SHED_ROOF | IfcRoof.SHED_ROOF | IfcRoof.SHED_ROOF
Roof | Gable roof | IfcRoof.GABLE_ROOF | IfcRoof.GABLE_ROOF | IfcRoof.GABLE_ROOF
Roof | Hip roof | IfcRoof.HIP_ROOF | IfcRoof.HIP_ROOF | IfcRoof.HIP_ROOF
Roof | Hipped gable roof | IfcRoof.HIPPED_GABLE_ROOF | IfcRoof.HIPPED_GABLE_ROOF | IfcRoof.HIPPED_GABLE_ROOF
Roof | Gambrel roof | IfcRoof.GAMBREL_ROOF | IfcRoof.GAMBREL_ROOF | IfcRoof.GAMBREL_ROOF
Roof | Mansard roof | IfcRoof.MANSARD_ROOF | IfcRoof.MANSARD_ROOF | IfcRoof.MANSARD_ROOF
Roof | Barrel roof | IfcRoof.BARREL_ROOF | IfcRoof.BARREL_ROOF | IfcRoof.BARREL_ROOF
Roof | Pavilion roof | IfcRoof.PAVILION_ROOF | IfcRoof.PAVILION_ROOF | IfcRoof.PAVILION_ROOF
Roof | Dome roof | IfcRoof.DOME_ROOF | IfcRoof.DOME_ROOF | IfcRoof.DOME_ROOF
Roof | Freeform | IfcRoof.FREEFORM | IfcRoof.FREEFORM | IfcRoof.FREEFORM
Roof | Pergola | IfcRoof.NOTDEFINED | IfcRoof.NOTDEFINED | IfcRoof.NOTDEFINED
Roof finishing | Stone cladding (marble, granite,etc.) | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Roof finishing | Cladding (metal, cassette, stone,etc.) | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Roof finishing | Roofing (slate, tile, zinc,etc.) | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Roof finishing | Metal tray | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Roof finishing | Sandwich panel | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Roof finishing | Battens | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Roof finishing | Levelling screed | IfcCovering.ROOFING | IfcCovering.ROOFING | IfcCovering.ROOFING
Safety lighting | Emergency lighting | IfcLightFixtureType.USERDEFINED[SECURITYLIGHTING] | IfcLightFixture.SECURITYLIGHTING | IfcLightFixture.SECURITYLIGHTING
Safety lighting | Emergency exit unit | IfcLightFixtureType.USERDEFINED[SECURITYLIGHTING] | IfcLightFixture.SECURITYLIGHTING | IfcLightFixture.SECURITYLIGHTING
Sanitary equipment | Bath | IfcSanitaryTerminalType.BATH | IfcSanitaryTerminal.BATH | IfcSanitaryTerminal.BATH
Sanitary equipment | Bidet | IfcSanitaryTerminalType.BIDET | IfcSanitaryTerminal.BIDET | IfcSanitaryTerminal.BIDET
Sanitary equipment | Flush | IfcSanitaryTerminalType.CISTERN | IfcSanitaryTerminal.CISTERN | IfcSanitaryTerminal.CISTERN
Sanitary equipment | Toilet bowl | IfcSanitaryTerminalType.TOILETPAN | IfcSanitaryTerminal.TOILETPAN | IfcSanitaryTerminal.TOILETPAN
Sanitary equipment | WC | IfcSanitaryTerminalType.TOILETPAN | IfcSanitaryTerminal.TOILETPAN | IfcSanitaryTerminal.TOILETPAN
Sanitary equipment | Toilet | IfcSanitaryTerminalType.TOILETPAN | IfcSanitaryTerminal.TOILETPAN | IfcSanitaryTerminal.TOILETPAN
Sanitary equipment | Dry toilet | IfcSanitaryTerminalType.TOILETPAN | IfcSanitaryTerminal.TOILETPAN | IfcSanitaryTerminal.TOILETPAN
Sanitary equipment | Sink | IfcSanitaryTerminalType.SINK | IfcSanitaryTerminal.SINK | IfcSanitaryTerminal.SINK
Sanitary equipment | Water fountain | IfcSanitaryTerminalType.SANITARYFOUNTAIN | IfcSanitaryTerminal.SANITARYFOUNTAIN | IfcSanitaryTerminal.SANITARYFOUNTAIN
Sanitary equipment | Hand wash basin | IfcSanitaryTerminalType.WASHHANDBASIN | IfcSanitaryTerminal.WASHHANDBASIN | IfcSanitaryTerminal.WASHHANDBASIN
Sanitary equipment | Shower tray | IfcSanitaryTerminalType.SHOWER | IfcSanitaryTerminal.SHOWER | IfcSanitaryTerminal.SHOWER
Sanitary equipment | Urinal | IfcSanitaryTerminalType.URINAL | IfcSanitaryTerminal.URINAL | IfcSanitaryTerminal.URINAL
Sanitary equipment | Washbasin | IfcSanitaryTerminalType.SINK | IfcSanitaryTerminal.SINK | IfcSanitaryTerminal.SINK
Sanitary/heating pipe | Rigid pipe | IfcPipeSegmentType.RIGIDSEGMENT | IfcPipeSegment.RIGIDSEGMENT | IfcPipeSegment.RIGIDSEGMENT
Sanitary/heating pipe | Flexible pipe | IfcPipeSegmentType.FLEXIBLESEGMENT | IfcPipeSegment.FLEXIBLESEGMENT | IfcPipeSegment.FLEXIBLESEGMENT
Sanitary/heating pipe fitting | Plug | IfcPipeFittingType.OBSTRUCTION | IfcPipeFitting.OBSTRUCTION | IfcPipeFitting.OBSTRUCTION
Sanitary/heating pipe fitting | Elbow | IfcPipeFittingType.BEND | IfcPipeFitting.BEND | IfcPipeFitting.BEND
Sanitary/heating pipe fitting | Shutter | IfcPipeFittingType.OBSTRUCTION | IfcPipeFitting.OBSTRUCTION | IfcPipeFitting.OBSTRUCTION
Sanitary/heating pipe fitting | Reducer | IfcPipeFittingType.TRANSITION | IfcPipeFitting.TRANSITION | IfcPipeFitting.TRANSITION
Sanitary/heating pipe fitting | Transition (section change) | IfcPipeFittingType.TRANSITION | IfcPipeFitting.TRANSITION | IfcPipeFitting.TRANSITION
Sanitary/heating pipe fitting | Junction (Y - T - X) | IfcPipeFittingType.JUNCTION | IfcPipeFitting.JUNCTION | IfcPipeFitting.JUNCTION
Sanitary/heating pipe fitting | Water manifold | IfcPipeFittingType.USERDEFINED[MANIFOLD] | IfcPipeFitting.USERDEFINED[MANIFOLD] | IfcPipeFitting.USERDEFINED[MANIFOLD]
Sanitary/heating pipe fitting | Heating manifold | IfcPipeFittingType.USERDEFINED[MANIFOLD] | IfcPipeFitting.USERDEFINED[MANIFOLD] | IfcPipeFitting.USERDEFINED[MANIFOLD]
Slab | Load bearing slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Balcony | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Landing | IfcSlab.LANDING | IfcSlab.LANDING | IfcSlab.LANDING
Slab | Load-bearing floor | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Roof | IfcSlab.ROOF | IfcSlab.ROOF | IfcSlab.ROOF
Slab | Hollowcore | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Concrete topping | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Compression concrete layer | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Concrete pre-slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Rib and block slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Hollow block slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | Composite slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab | TT slab | IfcSlab.FLOOR | IfcSlab.FLOOR | IfcSlab.FLOOR
Slab-on-grade | Slab-on-grade | IfcSlab.BASESLAB | IfcSlab.BASESLAB | IfcSlab.BASESLAB
Slab-on-grade | Baseslab | IfcSlab.BASESLAB | IfcSlab.BASESLAB | IfcSlab.BASESLAB
Slab-on-grade | Paving | IfcSlab.BASESLAB | IfcSlab.BASESLAB | IfcSlab.BASESLAB
Solar panel | Solar panel | IfcEnergyConversionDevice | IfcSolarDevice.SOLARCOLLECTOR | IfcSolarDevice.SOLARCOLLECTOR
Solar panel | Solar thermal collector | IfcEnergyConversionDevice | IfcSolarDevice.SOLARCOLLECTOR | IfcSolarDevice.SOLARCOLLECTOR
Solar panel | Solar collector | IfcEnergyConversionDevice | IfcSolarDevice.SOLARCOLLECTOR | IfcSolarDevice.SOLARCOLLECTOR
Solar panel | Photovoltaic module | IfcEnergyConversionDevice | IfcSolarDevice.SOLARPANEL | IfcSolarDevice.SOLARPANEL
Solar panel | Photovoltaic panel | IfcEnergyConversionDevice | IfcSolarDevice.SOLARPANEL | IfcSolarDevice.SOLARPANEL
Solar panel | Hybrid solar panel | IfcEnergyConversionDevice | IfcSolarDevice.USERDEFINED[HYBRID] | IfcSolarDevice.USERDEFINED[HYBRID]
Solar panel | Tracker | IfcEnergyConversionDevice | IfcSolarDevice.SOLARPANEL | IfcSolarDevice.SOLARPANEL
Space | Room | IfcSpace | IfcSpace | IfcSpace
Space | Parking | IfcSpace.USERDEFINED[PARKING] | IfcSpace.PARKING | IfcSpace.PARKING
Sprinkler | Sprinkler | IfcFireSuppressionTerminalType.SPRINKLER | IfcFireSuppressionTerminal.SPRINKLER | IfcFireSuppressionTerminal.SPRINKLER
Sprinkler | Automatic water extinguisher | IfcFireSuppressionTerminalType.SPRINKLER | IfcFireSuppressionTerminal.SPRINKLER | IfcFireSuppressionTerminal.SPRINKLER
Stair | Straight run stair | IfcStair.STRAIGHT_RUN_STAIR | IfcStair.STRAIGHT_RUN_STAIR | IfcStair.STRAIGHT_RUN_STAIR
Stair | Twostraight run stair | IfcStair.TWO_STRAIGHT_RUN_STAIR | IfcStair.TWO_STRAIGHT_RUN_STAIR | IfcStair.TWO_STRAIGHT_RUN_STAIR
Stair | Quarter winding stair | IfcStair.QUARTER_WINDING_STAIR | IfcStair.QUARTER_WINDING_STAIR | IfcStair.QUARTER_WINDING_STAIR
Stair | Quarter turn stair | IfcStair.QUARTER_TURN_STAIR | IfcStair.QUARTER_TURN_STAIR | IfcStair.QUARTER_TURN_STAIR
Stair | Half winding stair | IfcStair.HALF_WINDING_STAIR | IfcStair.HALF_WINDING_STAIR | IfcStair.HALF_WINDING_STAIR
Stair | Half turn stair | IfcStair.HALF_TURN_STAIR | IfcStair.HALF_TURN_STAIR | IfcStair.HALF_TURN_STAIR
Stair | Two quarter winding stair | IfcStair.TWO_QUARTER_WINDING_STAIR | IfcStair.TWO_QUARTER_WINDING_STAIR | IfcStair.TWO_QUARTER_WINDING_STAIR
Stair | Two quarter turn stair | IfcStair.TWO_QUARTER_TURN_STAIR | IfcStair.TWO_QUARTER_TURN_STAIR | IfcStair.TWO_QUARTER_TURN_STAIR
Stair | Three quarter winding stair | IfcStair.THREE_QUARTER_WINDING_STAIR | IfcStair.THREE_QUARTER_WINDING_STAIR | IfcStair.THREE_QUARTER_WINDING_STAIR
Stair | Three quarter turn stair | IfcStair.THREE_QUARTER_TURN_STAIR | IfcStair.THREE_QUARTER_TURN_STAIR | IfcStair.THREE_QUARTER_TURN_STAIR
Stair | Spiral stair | IfcStair.SPIRAL_STAIR | IfcStair.SPIRAL_STAIR | IfcStair.SPIRAL_STAIR
Stair | Double return stair | IfcStair.DOUBLE_RETURN_STAIR | IfcStair.DOUBLE_RETURN_STAIR | IfcStair.DOUBLE_RETURN_STAIR
Stair | Curved run stair | IfcStair.CURVED_RUN_STAIR | IfcStair.CURVED_RUN_STAIR | IfcStair.CURVED_RUN_STAIR
Stair | Two curved run stair | IfcStair.TWO_CURVED_RUN_STAIR | IfcStair.TWO_CURVED_RUN_STAIR | IfcStair.TWO_CURVED_RUN_STAIR
Stair | Free form stair | IfcStair.USERDEFINED[FREEFORM] | IfcStair.USERDEFINED[FREEFORM] | IfcStair.USERDEFINED[FREEFORM]
Tank | Fire fighting storage | IfcTankType.USERDEFINED[VESSEL] | IfcTank.VESSEL | IfcTank.VESSEL
Tank | Buffer tank | IfcTankType.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL
Tank | Dead water tank | IfcTankType.USERDEFINED[VESSEL] | IfcTank.VESSEL | IfcTank.VESSEL
Tank | Rain water harvesting | IfcTankType.USERDEFINED[BASIN] | IfcTank.BASIN | IfcTank.BASIN
Tank | Retention tank | IfcTankType.USERDEFINED[BASIN] | IfcTank.BASIN | IfcTank.BASIN
Tank | Pressure-breaking cylinder | IfcTankType.USERDEFINED[BREAKPRESSURE] | IfcTank.BREAKPRESSURE | IfcTank.BREAKPRESSURE
Tank | Rainwater tank | IfcTankType.USERDEFINED[STORAGE] | IfcTank.STORAGE | IfcTank.STORAGE
Tank | Grey water tank | IfcTankType.USERDEFINED[STORAGE] | IfcTank.STORAGE | IfcTank.STORAGE
Tank | Septic tank | IfcTankType.USERDEFINED[STORAGE] | IfcTank.STORAGE | IfcTank.STORAGE
Tank | Pressure tank (O2, CO2,etc.) | IfcTankType.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL
Tank | Expansion tank | IfcTankType.EXPANSION | IfcTank.EXPANSION | IfcTank.EXPANSION
Tank | Oil tank | IfcTankType.USERDEFINED[STORAGE] | IfcTank.STORAGE | IfcTank.STORAGE
Tank | Gas tank (natural gas, propane, etc.) | IfcTankType.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL | IfcTank.PRESSUREVESSEL
Tank | Sump | IfcTankType.USERDEFINED[STORAGE] | IfcTank.STORAGE | IfcTank.STORAGE
Technical floor | Technical floor | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Technical floor | False floor | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Technical floor | Raised floor | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Technical floor | Metal grating | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Transport equipment (excluding lifts) | Stair lift | IfcTransportElement.USERDEFINED[STAIR_LIFT] | IfcTransportElement.USERDEFINED[STAIR_LIFT] | IfcTransportElement.USERDEFINED[STAIR_LIFT]
Transport equipment (excluding lifts) | Freight lift | IfcTransportElement.ELEVATOR | IfcTransportElement.ELEVATOR | IfcTransportElement.ELEVATOR
Transport equipment (excluding lifts) | Derrick (load mast) | IfcTransportElement.USERDEFINED[LIFTINGGEAR] | IfcTransportElement.LIFTINGGEAR | IfcTransportElement.LIFTINGGEAR
Transport equipment (excluding lifts) | Escalator | IfcTransportElement.ESCALATOR | IfcTransportElement.ESCALATOR | IfcTransportElement.ESCALATOR
Transport equipment (excluding lifts) | Rubble chute | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE] | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE] | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE]
Transport equipment (excluding lifts) | Crane | IfcTransportElement.USERDEFINED[CRANEWAY] | IfcTransportElement.CRANEWAY | IfcTransportElement.CRANEWAY
Transport equipment (excluding lifts) | Facade gondola | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM]
Transport equipment (excluding lifts) | Lifting gear | IfcTransportElement.USERDEFINED[LIFTINGGEAR] | IfcTransportElement.LIFTINGGEAR | IfcTransportElement.LIFTINGGEAR
Transport equipment (excluding lifts) | Laundry chute | IfcTransportElement.USERDEFINED[LAUNDRY_PASS] | IfcTransportElement.USERDEFINED[LAUNDRY_PASS] | IfcTransportElement.USERDEFINED[LAUNDRY_PASS]
Transport equipment (excluding lifts) | Boarding bridge | IfcTransportElement.USERDEFINED[GATEWAY] | IfcTransportElement.USERDEFINED[GATEWAY] | IfcTransportElement.USERDEFINED[GATEWAY]
Transport equipment (excluding lifts) | Lifting platform | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM]
Transport equipment (excluding lifts) | Bridge crane | IfcTransportElement.USERDEFINED[CRANEWAY] | IfcTransportElement.CRANEWAY | IfcTransportElement.CRANEWAY
Transport equipment (excluding lifts) | Mechanical ramp | IfcTransportElement.MOVINGWALKWAY | IfcTransportElement.MOVINGWALKWAY | IfcTransportElement.MOVINGWALKWAY
Transport equipment (excluding lifts) | Pneumatic tube system | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM]
Transport equipment (excluding lifts) | Teletube | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM]
Transport equipment (excluding lifts) | Conveyor belt | IfcTransportElement.MOVINGWALKWAY | IfcTransportElement.MOVINGWALKWAY | IfcTransportElement.MOVINGWALKWAY
Transport equipment (excluding lifts) | Escape slide | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE] | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE] | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE]
Ventilation air terminal | Non adjustable vent diffuser | IfcAirTerminalType.DIFFUSER | IfcAirTerminal.DIFFUSER | IfcAirTerminal.DIFFUSER
Ventilation air terminal | Adjustable vent diffuser | IfcAirTerminalType.REGISTER | IfcAirTerminal.REGISTER | IfcAirTerminal.REGISTER
Ventilation air terminal | Linear grille | IfcAirTerminalType.LINEARGRILLE | IfcAirTerminal.LOUVRE | IfcAirTerminal.LOUVRE
Ventilation air terminal | Grille | IfcAirTerminalType.GRILLE | IfcAirTerminal.GRILLE | IfcAirTerminal.GRILLE
Ventilation duct | Rigid duct | IfcDuctSegmentType.RIGIDSEGMENT | IfcDuctSegment.RIGIDSEGMENT | IfcDuctSegment.RIGIDSEGMENT
Ventilation duct | Flexible duct | IfcDuctSegmentType.FLEXIBLESEGMENT | IfcDuctSegment.FLEXIBLESEGMENT | IfcDuctSegment.FLEXIBLESEGMENT
Ventilation duct connection | Ventilation duct connection | IfcDuctFittingType | IfcDuctFitting | IfcDuctFitting
Ventilation duct connection | Connection | IfcDuctFittingType.CONNECTOR | IfcDuctFitting.CONNECTOR | IfcDuctFitting.CONNECTOR
Ventilation duct connection | Elbow | IfcDuctFittingType.BEND | IfcDuctFitting.BEND | IfcDuctFitting.BEND
Ventilation duct connection | Junction (Y - T - X) | IfcDuctFittingType.JUNCTION | IfcDuctFitting.JUNCTION | IfcDuctFitting.JUNCTION
Ventilation duct connection | Shutter | IfcDuctFittingType.OBSTRUCTION | IfcDuctFitting.OBSTRUCTION | IfcDuctFitting.OBSTRUCTION
Ventilation duct connection | Reducer | IfcDuctFittingType.TRANSITION | IfcDuctFitting.TRANSITION | IfcDuctFitting.TRANSITION
Ventilation duct connection | Adapter | IfcDuctFittingType.TRANSITION | IfcDuctFitting.TRANSITION | IfcDuctFitting.TRANSITION
Ventilation silencer | Oval silencer | IfcDuctSilencerType.FLATOVAL | IfcDuctSilencer.FLATOVAL | IfcDuctSilencer.FLATOVAL
Ventilation silencer | Rectangular silencer | IfcDuctSilencerType.RECTANGULAR | IfcDuctSilencer.RECTANGULAR | IfcDuctSilencer.RECTANGULAR
Ventilation silencer | Round silencer | IfcDuctSilencerType.ROUND | IfcDuctSilencer.ROUND | IfcDuctSilencer.ROUND
Wall | Wall | IfcWall.STANDARD | IfcWall.STANDARD | IfcWall.STANDARD
Wall | Parapet | IfcWall.USERDEFINED[PARAPET] | IfcWall.PARAPET | IfcWall.PARAPET
Wall | Load-bearing masonry | IfcWall.USERDEFINED[SOLIDWALL] | IfcWall.SOLIDWALL | IfcWall.SOLIDWALL
Wall | Bracing masonry | IfcWall.SHEAR | IfcWall.SHEAR | IfcWall.SHEAR
Wall | Timber frame wall | IfcWall.ELEMENTEDWALL | IfcWall.ELEMENTEDWALL | IfcWall.ELEMENTEDWALL
Wall | Frost footing | IfcWall.USERDEFINED[SOLIDWALL] | IfcWall.SOLIDWALL | IfcWall.SOLIDWALL
Wall | Frost wall | IfcWall.USERDEFINED[SOLIDWALL] | IfcWall.SOLIDWALL | IfcWall.SOLIDWALL
Wall | Partition | IfcWall.USERDEFINED[PARTITIONNING] | IfcWall.PARTITIONING | IfcWall.PARTITIONING
Wall | Movable wall | IfcWall.USERDEFINED[MOVABLE] | IfcWall.MOVABLE | IfcWall.MOVABLE
Wall | Thermal break (structural) | IfcWall.USERDEFINED[INSULATION] | IfcWall.USERDEFINED[INSULATION] | IfcWall.USERDEFINED[INSULATION]
Wall | Insulating masonry | IfcWall.USERDEFINED[SOLIDWALL] | IfcWall.SOLIDWALL | IfcWall.SOLIDWALL
Wall | Toilet partition | IfcWall.STANDARD | IfcWall.STANDARD | IfcWall.STANDARD
Wall | Technical space closure | IfcWall.PLUMBINGWALL | IfcWall.PLUMBINGWALL | IfcWall.PLUMBINGWALL
Wall | Precast concrete wall | IfcWall.USERDEFINED[SOLIDWALL] | IfcWall.SOLIDWALL | IfcWall.SOLIDWALL
Wall | Secant pile | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Tangeant pile | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Sheet pile | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Retaining wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Deepwall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Diaphragm wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Slurry wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Soldier pile wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Lagging wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Combiwall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Soilmix wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Cement-bentonite slurry wall | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Timbered trench | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall | Shored trench | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL] | IfcWall.USERDEFINED[RETAININGWALL]
Wall finishing | Cladding (metal, cassette, stone,etc.) | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Plaster (plaster, clay, lime, cement,etc.) | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Stone cladding (marble, granite, etc.) | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Tiling | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Masonry cladding | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Carpet | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Finishing panel | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Plasterboard | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Plinth | IfcCovering.USERDEFINED[SKIRTINGBOARD] | IfcCovering.SKIRTINGBOARD | IfcCovering.SKIRTINGBOARD
Wall finishing | Baseboard | IfcCovering.USERDEFINED[SKIRTINGBOARD] | IfcCovering.SKIRTINGBOARD | IfcCovering.SKIRTINGBOARD
Wall finishing | Cornice (exterior) | IfcCovering.USERDEFINED[MOLDING] | IfcCovering.MOLDING | IfcCovering.MOLDING
Wall finishing | Molding (interior) | IfcCovering.USERDEFINED[MOLDING] | IfcCovering.MOLDING | IfcCovering.MOLDING
Wall finishing | Sandwich panel | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Battens | IfcCovering.CLADDING | IfcCovering.CLADDING | IfcCovering.CLADDING
Wall finishing | Wall protection | IfcCovering.USERDEFINED[SHOCKISOLATOR] | IfcCovering.USERDEFINED[SHOCKISOLATOR] | IfcCovering.USERDEFINED[SHOCKISOLATOR]
Wall finishing | Wall painting | IfcCovering.USERDEFINED[PAINTING] | IfcCovering.USERDEFINED[WALL_PAINTING] | IfcCovering.USERDEFINED[PAINTING]
Water collector | Gutter | IfcPipeSegmentType.GUTTER | IfcPipeSegment.GUTTER | IfcPipeSegment.GUTTER
Water collector | Water channel | IfcPipeSegmentType.GUTTER | IfcPipeSegment.GUTTER | IfcPipeSegment.GUTTER
Window | Window | IfcWindow | IfcWindow | IfcWindow
Window | Skylight dome | IfcWindow | IfcWindow.LIGHTDOME | IfcWindow.LIGHTDOME
Window | Roof window | IfcWindow | IfcWindow.LIGHTDOME | IfcWindow.LIGHTDOME
Window | Smoke extraction window | IfcWindow | IfcWindow.SKYLIGHT | IfcWindow.SKYLIGHT
Zone | Zone | IfcZone | IfcZone | IfcZone
Zone | Wing | IfcZone | IfcZone | IfcZone
Zone | Appartment | IfcZone | IfcZone | IfcZone
Zone | Block | IfcZone | IfcZone | IfcZone
Zone | Group | IfcZone | IfcZone | IfcZone
Zone | Unit (hospital) | IfcZone | IfcZone | IfcZone

## Actuator
Actuator
Return to overview
General
An actuator is a mechanical device for moving or controlling a mechanism or system. An actuator takes energy, usually created by air, electricity, or liquid, and converts it into one or the other type of motion.
Other data sheet GTB : management panel.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Shutter/blind motor |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Door closer |  | IfcActuatorType.HANDOPERATEDACTUATOR | [5 empty] | IfcActuator.HANDOPERATEDACTUATOR |  | IfcActuator.HANDOPERATEDACTUATOR
Motorised door closer (door opener) |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Magnetic contact (door strike or holder) |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Motorised lock |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Mechanical lock |  | IfcActuatorType.HANDOPERATEDACTUATOR | [5 empty] | IfcActuator.HANDOPERATEDACTUATOR |  | IfcActuator.HANDOPERATEDACTUATOR
Compressed air motor smoke vent |  | IfcActuatorType.PNEUMATICACTUATOR | [5 empty] | IfcActuator.PNEUMATICACTUATOR |  | IfcActuator.PNEUMATICACTUATOR
Electric motor smoke outlet |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Magnetic lock |  | IfcActuatorType.ELECTRICACTUATOR | [5 empty] | IfcActuator.ELECTRICACTUATOR |  | IfcActuator.ELECTRICACTUATOR
Hydraulic mechanism (opening, support,etc.) |  | IfcActuatorType.HYDRAULICACTUATOR | [5 empty] | IfcActuator.HYDRAULICACTUATOR |  | IfcActuator.HYDRAULICACTUATOR
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Electrical design (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X
Width |  |  |  |  | X
Height |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3 | Alles onder alphanumerical niet rood moet toegevoegd worden, als begint met BIMids custom property niet in IFC, als met Pset link maken met IFC via URI.
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_DistributionControlElementTypeCommon.Status1 |  | Pset_ActuatorTypeCommon.Status |  | Pset_ActuatorTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X | X | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D8010.10 – Integrated Automation Control of Equipment D8010.20 – Integrated Automation Control of Conveying Equipment D8010.30 – Integrated Automation Control of Fire-Suppression Systems D8010.40 – Integrated Automation Control of Plumbing Systems D8010.50 – Integrated Automation Control of HVAC Systems D8010.60 – Integrated Automation Control of Electrical Systems D8010.70 – Integrated Automation Control of Communication Systems D8010.80 – Integrated Automation Control of Electronic Safety and Security Systems D8010.90 – Integrated Automation Supplementary Components
DIN276 |  | KG 466 – hydraulikanlagen KG 481 – Automationseinrichtungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Air handling unit
Air handling unit
Return to overview
General
An air handling unit comprises several components, serving in particular to filter, heat, cool, humidify or dehumidify air and then distribute it in a building. An AHU can be a single integrated whole or composed of modules aggregated as needed.
Other data sheets for ventilation elements: air-to-air exchanger, filter, fan, vantilation duct, ventilation duct connection, vent.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Air handling unit (ahu) |  | IfcUnitaryEquipmentType.AIRHANDLER | [5 empty] | IfcUnitaryEquipment.AIRHANDLER |  | IfcUnitaryEquipment.AIRHANDLER
Air-to-air heat pump (including reversible) |  | IfcUnitaryEquipmentType.SPLITSYSTEM | [5 empty] | IfcUnitaryEquipment.SPLITSYSTEM |  | IfcUnitaryEquipment.SPLITSYSTEM
Dehumidifier |  | IfcUnitaryEquipmentType.USERDEFINED[DEHUMIDIFIER] | [5 empty] | IfcUnitaryEquipment.DEHUMIDIFIER |  | IfcUnitaryEquipment.DEHUMIDIFIER
The sub-components of an IfcUnitaryEquipment can be as follows, on a case-by-case basis:
- Motorr : IFc FlowMovingDevice (IFC2x3) or IfcFan (IFC4), voir Ventilation - fan
- Humidifier : IfcEnergyConversionDevice (Ifc2x3) or IfcHumidifier (IFC4)
- Heat generation: IfcBoiler, see Heat production - water and Heat production - steam
- Cooling generation: IfcChiller, see Cooling - cooling generation
- Heat exchanger (other than air/air): IfcEnergyConversionDevice (Ifc2x3) or IfcHeatExchanger (IFC4)
- Air/air heat exchanger: IfcEnergyConversionDevice (Ifc2x3) or IfcAirToAirHeatRecovery (IFC4), see Ventilation - air-air exchanger
- Filter : IfcFlowTreatementDevice (IFC2x3) or IfcFilter (IFC4)
- Tank: IfcTank, see Tank
- Control valve: IfcValve (IFC4)
- Damper valve: IFCDamper (IFC4)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_UnitaryEquipmentTypeCommon.Status |  | Pset_UnitaryEquipmentTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3020 – Heating System D3030 – Cooling System
DIN276 |  | KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Air handling unit

## Air-to-air exchanger
Air-to-air exchanger
Return to overview
General
An air-to-air exchanger is a device serving to transfer heat between 2 crossed air flows. The classic example is dual-flow mechanical ventilation with heat recovery, via such an exchanger. Here the heat from the air extracted from the building is transferred to the fresh air entering from outside for injection into the building during the heating period.
Other data sheets for ventilation elements: fan, filter, air handling unit, ventilmation duct connection, ventilation duct, vent.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Counterflow plate heat exchanger |  | IfcAirToAirHeatRecoveryType.FIXEDPLATECOUNTERFLOWEXCHANGER | [5 empty] | IfcAirToAirHeatRecovery.FIXEDPLATECOUNTERFLOWEXCHANGER |  | IfcAirToAirHeatRecovery.FIXEDPLATECOUNTERFLOWEXCHANGER
Cross flow plate heat exchanger |  | IfcAirToAirHeatRecoveryType.FIXEDPLATECROSSFLOWEXCHANGER | [5 empty] | IfcAirToAirHeatRecovery.FIXEDPLATECROSSFLOWEXCHANGER |  | IfcAirToAirHeatRecovery.FIXEDPLATECROSSFLOWEXCHANGER
Parallel flow plate heat exchanger |  | IfcAirToAirHeatRecoveryType.FIXEDPLATEPARALLELFLOWEXCHANGER | [5 empty] | IfcAirToAirHeatRecovery.FIXEDPLATEPARALLELFLOWEXCHANGER |  | IfcAirToAirHeatRecovery.FIXEDPLATEPARALLELFLOWEXCHANGER
Wheel heat exchanger |  | IfcAirToAirHeatRecoveryType.ROTARYWHEEL | [5 empty] | IfcAirToAirHeatRecovery.ROTARYWHEEL |  | IfcAirToAirHeatRecovery.ROTARYWHEEL
Tube heat exchanger |  | IfcAirToAirHeatRecoveryType.RUNAROUNDCOILLOOP | [5 empty] | IfcAirToAirHeatRecovery.RUNAROUNDCOILLOOP |  | IfcAirToAirHeatRecovery.RUNAROUNDCOILLOOP
Enthalpy exchanger |  | IfcAirToAirHeatRecoveryType.TWINTOWERENTHALPYRECOVERYLOOPS | [5 empty] | IfcAirToAirHeatRecovery.TWINTOWERENTHALPYRECOVERYLOOPS |  | IfcAirToAirHeatRecovery.TWINTOWERENTHALPYRECOVERYLOOPS
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_AirToAirHeatRecoveryTypeCommon.Status |  | Pset_AirToAirHeatRecoveryTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Total effectiveness |  |  |  |  | X | X | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness
PEB (partial requirements)
Total effectiveness |  |  | X | X | X | X | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness
Sanitary/HVAC design (partial requirements)
Total effectiveness |  |  | X | X | X | X | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness |  | Pset_AirToAirHeatRecoveryPHistory.TotalEffectiveness
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  | X | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3060.60 – Air-to-Air Energy Recovery
DIN276 |  | KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Air-to-air exchanger

## Audiovisual device
Audiovisual device
Return to overview
General
An audio-visual appliance is a device that displays, captures, transmits, or receives audio or video. Audio-visual appliances may be fixed in place or may be able to be moved from one space to another. They may require an electrical supply that may be supplied either by an electrical circuit or provided from a local battery source. Audio-visual appliances may be connected to data circuits including specialist circuits for audio-visual purposes only.
Other data sheet relating to electrical appliances: data device, electric appliance.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Power amplifier |  | IfcElectricApplianceType.USERDEFINED[AMPLIFIER] | [5 empty] | IfcAudioVisualAppliance.AMPLIFIER |  | IfcAudioVisualAppliance.AMPLIFIER
Integrated amplifier |  | IfcElectricApplianceType.USERDEFINED[AMPLIFIER] | [5 empty] | IfcAudioVisualAppliance.AMPLIFIER |  | IfcAudioVisualAppliance.AMPLIFIER
Audio-video switch |  | IfcElectricApplianceType.USERDEFINED[SWITCHER] | [5 empty] | IfcAudioVisualAppliance.SWITCHER |  | IfcAudioVisualAppliance.SWITCHER
Screen |  | IfcElectricApplianceType.TV | [5 empty] | IfcAudioVisualAppliance.DISPLAY |  | IfcAudioVisualAppliance.DISPLAY
Speaker |  | IfcElectricApplianceType.USERDEFINED[SPEAKER] | [5 empty] | IfcAudioVisualAppliance.SPEAKER |  | IfcAudioVisualAppliance.SPEAKER
Alarm speaker (fire/voice alarm) |  | IfcElectricApplianceType.USERDEFINED[SPEAKER] | [5 empty] | IfcAudioVisualAppliance.SPEAKER |  | IfcAudioVisualAppliance.SPEAKER
Media player |  | IfcElectricApplianceType.USERDEFINED[PLAYER] | [5 empty] | IfcAudioVisualAppliance.PLAYER |  | IfcAudioVisualAppliance.PLAYER
Television |  | IfcElectricApplianceType.TV | [5 empty] | IfcAudioVisualAppliance.DISPLAY |  | IfcAudioVisualAppliance.DISPLAY
TV |  | IfcElectricApplianceType.TV | [5 empty] | IfcAudioVisualAppliance.DISPLAY |  | IfcAudioVisualAppliance.DISPLAY
Camera |  | IfcElectricApplianceType.USERDEFINED[CAMERA] | [5 empty] | IfcAudioVisualAppliance.CAMERA |  | IfcAudioVisualAppliance.CAMERA
Camera |  | IfcElectricApplianceType.USERDEFINED[CAMERA] | [5 empty] | IfcAudioVisualAppliance.CAMERA |  | IfcAudioVisualAppliance.CAMERA
Camera ip |  | IfcElectricApplianceType.USERDEFINED[CAMERA] | [5 empty] | IfcAudioVisualAppliance.CAMERA |  | IfcAudioVisualAppliance.CAMERA
Dome camera |  | IfcElectricApplianceType.USERDEFINED[CAMERA] | [5 empty] | IfcAudioVisualAppliance.CAMERA |  | IfcAudioVisualAppliance.CAMERA
video conferencing camera |  | IfcElectricApplianceType.USERDEFINED[CAMERA] | [5 empty] | IfcAudioVisualAppliance.CAMERA |  | IfcAudioVisualAppliance.CAMERA
Intercom |  | IfcElectricApplianceType.USERDEFINED[INTERCOM] | [5 empty] | IfcAudioVisualAppliance.USERDEFINED[INTERCOM] |  | IfcAudioVisualAppliance.USERDEFINED[INTERCOM]
Video intercom |  | IfcElectricApplianceType.USERDEFINED[VIDEOINTERCOM] | [5 empty] | IfcAudioVisualAppliance.USERDEFINED[VIDEOINTERCOM] |  | IfcAudioVisualAppliance.USERDEFINED[VIDEOINTERCOM]
Video decoder |  | IfcElectricApplianceType.USERDEFINED[TUNER] | [5 empty] | IfcAudioVisualAppliance.TUNER |  | IfcAudioVisualAppliance.TUNER
TV box |  | IfcElectricApplianceType.USERDEFINED[TUNER] | [5 empty] | IfcAudioVisualAppliance.TUNER |  | IfcAudioVisualAppliance.TUNER
Microphone |  | IfcElectricApplianceType.USERDEFINED[MICROPHONE] | [5 empty] | IfcAudioVisualAppliance.MICROPHONE |  | IfcAudioVisualAppliance.MICROPHONE
Radio tuner |  | IfcElectricApplianceType.USERDEFINED[TUNER] | [5 empty] | IfcAudioVisualAppliance.TUNER |  | IfcAudioVisualAppliance.TUNER
Projector |  | IfcElectricApplianceType.USERDEFINED[PROJECTOR] | [5 empty] | IfcAudioVisualAppliance.PROJECTOR |  | IfcAudioVisualAppliance.PROJECTOR
Telephone |  | IfcElectricApplianceType.TELEPHONE | [5 empty] | IfcAudioVisualAppliance.TELEPHONE |  | IfcAudioVisualAppliance.TELEPHONE
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ElectericApplianceTypeCommon.Status1 |  | Pset_AudioVisualApplianceTypeCommon.Status |  | Pset_AudioVisualApplianceTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_ElectricApplianceTypeCommon.Status1 |  | Pset_AudioVisualApplianceTypeCommon.Status |  | Pset_AudioVisualApplianceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D6020 - Voice Communications D6030 – Audio-Video Communication
DIN276 |  | KG451 – Telekommunikationsanlagen KG452 – Such- und Signalanlagen KG454 – Elektroackustische Anlagen KG455 – Audiovisuelle Medien- und Antennenanlagen KG483 – Automationsmanagement
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Audiovisual device

## Beam
Beam
Return to overview
General
A beam is a generally horizontal (sometimes oblique) linear construction element serving to pick up linear or concentrated loads – mainly vertical but sometimes horizontal – by bending above an opening and to transmit them to the structural elements below (columns, walls. ..). Beams also cover lattice beams, composed of several inter-articulated linear structural elements forming a triangulation (frame member)
Other data sheets for linear structural elements : beam foundation, linear structural member, column.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Metal girder |  | IfcBeam.BEAM | [5 empty] | IfcBeam.BEAM |  | IfcBeam.BEAM
Ring beam |  | IfcBeam.USERDEFINED[RING_BEAM] | [5 empty] | IfcBeam.USERDEFINED[RING_BEAM] |  | IfcBeam.USERDEFINED[RING_BEAM]
Floor support beam |  | IfcBeam.JOIST | [5 empty] | IfcBeam.JOIST |  | IfcBeam.JOIST
Lintel |  | IfcBeam.LINTEL | [5 empty] | IfcBeam.LINTEL |  | IfcBeam.LINTEL
Spandrel beam |  | IfcBeam.USERDEFINED[SPANDREL] | [5 empty] | IfcBeam.SPANDREL |  | IfcBeam.SPANDREL
Inverted beam |  | IfcBeam.USERDEFINED[SPANDREL] | [5 empty] | IfcBeam.SPANDREL |  | IfcBeam.SPANDREL
Castellated beam |  | IfcBeam.BEAM | [5 empty] | IfcBeam.BEAM |  | IfcBeam.BEAM
Cellular beam |  | IfcBeam.BEAM | [5 empty] | IfcBeam.BEAM |  | IfcBeam.BEAM
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Slope |  |  | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Slope |  |  |  | X | X
Section profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Fire safety (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Architectural design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Slope |  |  |  |  | X
Section profile |  |  | X |  | X
Acoustics (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Clash detection (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Section profile |  |  |  | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_BeamCommon.Status1 |  | Pset_BeamCommon.Status |  | Pset_BeamCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_BeamCommon.Status |  | Pset_BeamCommon.Status |  | Pset_BeamCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | Pset_BeamCommon.LoadBearing |  | Pset_BeamCommon.LoadBearing |  | Pset_BeamCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_BeamCommon.IsExternal |  | Pset_BeamCommon.IsExternal |  | Pset_BeamCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  | X |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | Pset_BeamCommon.ThermalTransmittance |  | Pset_BeamCommon.ThermalTransmittance |  | Pset_BeamCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_BeamCommon.FireRating |  | Pset_BeamCommon.FireRating |  | Pset_BeamCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Stability report |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1010.10 – Floor Structural Frame B1020.10 – Roof Structural Frame B2010.20 – Exterior Wall Construction B3080.10 – Exterior Ceiling C1010 – Interior Partition F1020.40 – Metal Building Systems
DIN276 |  | 331 – Tragende Außenwände 351 – Deckenkonstruktionen 355 – Elementierte Deckenkonstruktionen 361 – Dachkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Breeching inlet
Breeching inlet
Return to overview
General
A coupler is a connection system intended to supply the fire extinguisher network. These connectors are generally found outside the building for the connection of a water supply (via fire truck for example).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Breeching inlet |  | IfcFireSuppressionTerminalType.BREECHINGINLET | [5 empty] | IfcFireSuppressionTerminal.BREECHINGINLET |  | IfcFireSuppressionTerminal.BREECHINGINLET
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Insulation - thickness |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type of coupler |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType
Inlet diameter |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter
Outlet diameter |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter
Type of coupling |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType
Has caps |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps |  | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps |  | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps
Fire safety (partial requirements)
Type of coupler |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.BreechingInletType
Inlet diameter |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.InletDiameter
Outlet diameter |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter |  | Pset_FireSuppressionTerminalTypeBreechingInlet.OutletDiameter
Type of coupling |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType |  | Pset_FireSuppressionTerminalTypeBreechingInlet.CouplingType
Has caps |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps |  | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps |  | Pset_FireSuppressionTerminalTypeBreechingInlet.HasCaps
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4010 – Fire Suppression
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Breeching inlet

## Cable tray
Cable tray
Return to overview
General
A cable tray is a device permitting the passage of electrical cables. These can be hung on the wall/ceiling or placed on the floor. We can distinguish perforated sheet metal (open or closed) models, wire or ladder models and closed models. This data sheet covers only straight sections of cable trays, see below for other cable tray components.
Other data sheets for cable tray : cable tray connection.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Cable tray |  | IfcCableCarrierSegmentType.CABLETRAYSEGMENT | [5 empty] | IfcCableCarrierSegment.CABLETRAYSEGMENT |  | IfcCableCarrierSegment.CABLETRAYSEGMENT
Closed cable tray |  | IfcCableCarrierSegmentType.CABLETRUNKINGSEGMENT | [5 empty] | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT |  | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT
Cable ladder |  | IfcCableCarrierSegmentType.CABLELADDERSEGMENT | [5 empty] | IfcCableCarrierSegment.CABLELADDERSEGMENT |  | IfcCableCarrierSegment.CABLELADDERSEGMENT
Electrical trunking |  | IfcCableCarrierSegmentType.CONDUITSEGMENT | [5 empty] | IfcCableCarrierSegment.CONDUITSEGMENT |  | IfcCableCarrierSegment.CONDUITSEGMENT
Technical channel |  | IfcCableCarrierSegmentType.CABLETRUNKINGSEGMENT | [5 empty] | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT |  | IfcCableCarrierSegment.CABLETRUNKINGSEGMENT
Rigid protection tube (exposed cable) |  | IfcCableCarrierSegmentType.CONDUITSEGMENT | [5 empty] | IfcCableCarrierSegment.CONDUITSEGMENT |  | IfcCableCarrierSegment.CONDUITSEGMENT
Corrugated sheath |  | IfcCableCarrierSegmentType.CONDUITSEGMENT | [5 empty] | IfcCableCarrierSegment.CONDUITSEGMENT |  | IfcCableCarrierSegment.CONDUITSEGMENT
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Electrical design (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_CableCarrierSegmentTypeCommon.Status1 |  | Pset_CableCarrierSegmentTypeCommon.Status |  | Pset_CableCarrierSegmentTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Fire safety (partial requirements)
Fire rating |  |  |  | X | X | X | ePset_CableCarrierSegmentTypeCommon.FireRating1 |  | Pset_CableCarrierSegmentTypeCommon.FireRating |  | Pset_CableCarrierSegmentTypeCommon.FireRating
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | ePset_CableCarrierSegmentTypeCommon.FireRating1 |  | Pset_CableCarrierSegmentTypeCommon.FireRating |  | Pset_CableCarrierSegmentTypeCommon.FireRating
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.30 – Power Distribution D5020.90 – Electrical Service and Distribution Supplementary Components D5030.10 – Branch Wiring System D5030.90 – General Purpose Electrical Power Supplementary Components D5040.20 – Branch Wiring for Lighting D5040.90 – Lighting Supplementary Components D5080.90 – Miscellaneous Electrical Systems Supplementary Components D6090.10 – Supplementary Components
DIN276 |  | KG 444 – Niederspannungsinstallationsanlagen KG 445 – Beleuchtungsanlagen KG 451 – Telekommunikationsanlagen KG 454 – Elektroakustische Anlagen KG 455 – Audiovisuelle Medien- und Antennenanlagen KG 457 – Datenübertragungsnetze KG 484 – Kabel, Leitungen und Verlegesysteme
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.

## Cable tray connection
Cable tray connection
Return to overview
General
A cable tray is a device permitting the passage of electrical cables. These can be hung on the wall/ceiling or placed on the floor. We can distinguish perforated sheet metal (open or closed) models, wire or ladder models and closed models. This data sheet covers only the connectors between straight sections such as corners, T-connectors, 4-branch connectors and reductions, see below for the straight elements of the cable trays.
Other data sheets for cable tray: cable tray.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
4-way crossing |  | IfcCableCarrierFittingType.CROSS | [5 empty] | IfcCableCarrierFitting.CROSS |  | IfcCableCarrierFitting.JUNCTION
Corner fitting |  | IfcCableCarrierFittingType.BEND | [5 empty] | IfcCableCarrierFitting.BEND |  | IfcCableCarrierFitting.BEND
T-fitting |  | IfcCableCarrierFittingType.TEE | [5 empty] | IfcCableCarrierFitting.TEE |  | IfcCableCarrierFitting.JUNCTION
Reduction |  | IfcCableCarrierFittingType.REDUCER | [5 empty] | IfcCableCarrierFitting.REDUCER |  | IfcCableCarrierFitting.TRANSITION
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Electrical design (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_CableCarrierFittingTypeCommon.Status1 |  | Pset_CableCarrierFittingTypeCommon.Status |  | Pset_CableCarrierFittingTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Fire safety (partial requirements)
Fire rating |  |  |  | X | X | X | ePset_CableCarrierFittingTypeCommon.FireRating1 |  | Pset_CableCarrierFittingTypeCommon.FireRating |  | Pset_CableCarrierFittingTypeCommon.FireRating
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | ePset_CableCarrierFittingTypeCommon.FireRating1 |  | Pset_CableCarrierFittingTypeCommon.FireRating |  | Pset_CableCarrierFittingTypeCommon.FireRating
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.30 – Power Distribution D5020.90 – Electrical Service and Distribution Supplementary Components D5030.10 – Branch Wiring System D5030.90 – General Purpose Electrical Power Supplementary Components D5040.20 – Branch Wiring for Lighting D5040.90 – Lighting Supplementary Components D5080.90 – Miscellaneous Electrical Systems Supplementary Components D6090.10 – Supplementary Components
DIN276 |  | KG 444 – Niederspannungsinstallationsanlagen KG 445 – Beleuchtungsanlagen KG 451 – Telekommunikationsanlagen KG 454 – Elektroakustische Anlagen KG 455 – Audiovisuelle Medien- und Antennenanlagen KG 457 – Datenübertragungsnetze KG 484 – Kabel, Leitungen und Verlegesysteme
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Cable tray connection

## Caisson foundation
Caisson foundation
Return to overview
General
A caisson is a deep foundation that transmits the loads of a structure to the deeper layers of the ground. The load is transmitted by lateral friction and/or at the point. This type of structure is used when the loads to be transmitted to the ground are too great to work with direct foundations and/or when the bearing capacity of the upper layers of the ground is too low.
Other sheets for deep foundations : pile, beam foundation.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Caisson foundation |  | IfcFooting.USERDEFINED[CAISSON_FOUNDATION] | [5 empty] | IfcFooting.CAISSON_FOUNDATION |  | IfcFooting.CAISSON_FOUNDATION
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
2D documents (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Clash detection (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Fire safety (partial requirements)
Accessories and specific elements |  |  |  | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | ePset_FootingCommon.LoadBearing1 |  | Pset_FootingCommon.LoadBearing |  | Pset_FootingCommon.LoadBearing
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Geotechnical study report | X |  | X | X | X | X
Stability report |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A1020.20 – Caissons
DIN276 |  | 323 – Tiefgründungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Ceiling finishing
Ceiling finishing
Return to overview
General
This sheet contains all the finishing layers for ceilings. These are always non-load bearing layers.
Generally, the layers are modelled as multi-layers and the IFC export keeps these multi-layered walls, including the finishes. However, in some cases it is useful to have separate layers, and it is in these cases that the present GID sheet should be used :
- Spot finishing on a ceiling, e.g. a tiling on a partial area of a floor in a room in the middle of tiling, modelled with a single layer "slab" overlaying the general multi-layer slab.
- Need to have each layer separate in the IFC model (quantity extraction, work tracking by materials...). It is possible to break down the layers into individual objects when exporting IFC. Depending on the software you can specify an IFC class and type for each layer (PARTS Revit), the class is fixed in other software (Archicad, Allplan...).
- If the native modelling has been done layer by layer, then the mapping will have to be specified layer by layer, each layer being an independent IFC object.
Other related sheets : floor finishing, wall finishing, roof finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Ceiling finishing |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Plasterboard |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Tiling |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Stone cladding (marble, granite,etc.) |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Cladding (metal, cassette, stone,etc.) |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Plaster (plaster, clay, lime, cement,etc.) |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Metal tray |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Sandwich panel |  | IfcCovering.CEILING | [5 empty] | IfcCovering.CEILING |  | IfcCovering.CEILING
Battens |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Ceiling paint |  | IfcCovering.USERDEFINED[PAINTING] | [5 empty] | IfcCovering.USERDEFINED[CEILING_PAINTING] |  | IfcCovering.USERDEFINED[PAINTING]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Peripheral profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  |  |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_WallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Layout plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | C2050 – Ceiling finishing
DIN276 |  | 354 – Deckenbekleidungen 364 – Dachbegleidungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Ceiling finishing

## Chiller
Chiller
Return to overview
General
A cooling generator is a device used to extract heat from a liquid via a refrigeration cycle (vapour compression or absorption) to cool a fluid, usually water or a mixture of water and glycol. The cooled fluid then serves to cool and dehumidify the air in a building by blowing (via ventilation system, cold beam, etc.) or by radiation (cold ceiling/floor).
Other related data sheets: air handling unit, heat production - water, heat production - steam, heat/cold diffusion - surface, heat/cold diffusion - convector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Air conditioner |  | IfcChillerType.AIRCOOLED | [5 empty] | IfcChiller.AIRCOOLED |  | IfcChiller.AIRCOOLED
The sub-components of an IfcUnitaryEquipment can be:
- Evaporator : IfcEnergyConversionDevice/IfcEvaporatorType (IFC2x3) and IfcEvaporator (IFC4)
- Evaporative cooler: IfcEnergyConversionDevice/IfcEvaporativeCoolerType (IFC2x3) and IfcEvaporativeCooler (IFC4)
- Cooling tower : IfcEnergyConversionDevice/IfcCoolingTowerType (IFC2x3) and IfcCoolingTower (IFC4)
- Condenser : IfcEnergyConversionDevice/IfcCondenserType (IFC2x3) and IfcCondenser (IFC4)
- Compressor : IfcFlowMovingDevice/IfcCompressorType (IFC2x3) and IfcCompressor (IFC4)
- Pressure reducer: IfcFlowController/IfcValveType type PRESSUREREDUCING (IFC2x3) and IfcValve type PRESSUREREDUCING (IFC4)
- Heat exchanger: IfcEnergyConversionDevice/IfcHeatExchangerType (IFC2x3) and IfcHeatExchanger (IFC4)
- Humidifier : IfcEnergyConversionDevice/IfcHumidifierType (IFC2x3) and IfcHumidifier (IFC4)
- Valves: IfcFlowController/IfcValveType (IFC2x3) and IfcValve (IFC4)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_ChillerTypeCommon.Status |  | Pset_ChillerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Nominal power |  |  |  |  | X | X | ePset_ChillerTypeCommon.NominalCapacity1 |  | Pset_ChillerTypeCommon.NominalCapacity |  | Pset_ChillerTypeCommon.NominalCapacity
Nominal electric power |  |  |  |  | X | X | ePset_ChillerTypeCommon.NominalPowerConsumption1 |  | Pset_ChillerTypeCommon.NominalPowerConsumption |  | Pset_ChillerTypeCommon.NominalPowerConsumption
Capacity |  |  |  |  | X | X | Pset_ChillerPHistory.Capacity |  | Pset_ChillerPHistory.Capacity |  | Pset_ChillerPHistory.Capacity
Energy efficiency |  |  |  |  | X | X | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio
Sensible cooling capacity |  |  |  |  | X | X | ePset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity1 |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity
PEB (partial requirements)
Nominal power |  |  | X | X | X | X | ePset_ChillerTypeCommon.NominalCapacity1 |  | Pset_ChillerTypeCommon.NominalCapacity |  | Pset_ChillerTypeCommon.NominalCapacity
Nominal electric power |  |  | X | X | X | X | ePset_ChillerTypeCommon.NominalPowerConsumption1 |  | Pset_ChillerTypeCommon.NominalPowerConsumption |  | Pset_ChillerTypeCommon.NominalPowerConsumption
Energy efficiency | [5 empty] | X | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio
Sensible cooling capacity |  |  | X | X | X | X | ePset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity1 |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity
Sanitary/HVAC design (partial requirements)
Nominal electric power |  |  | X | X | X | X | ePset_ChillerTypeCommon.NominalPowerConsumption1 |  | Pset_ChillerTypeCommon.NominalPowerConsumption |  | Pset_ChillerTypeCommon.NominalPowerConsumption
Capacity |  |  |  |  | X | X | Pset_ChillerPHistory.Capacity |  | Pset_ChillerPHistory.Capacity |  | Pset_ChillerPHistory.Capacity
Energy efficiency |  |  |  |  | X | X | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio |  | Pset_ChillerPHistory.EnergyEfficiencyRatio
Sensible cooling capacity |  |  | X | X | X | X | ePset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity1 |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity |  | Pset_UnitaryEquipmentTypeAirConditioningUnit.SensibleCoolingCapacity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3030.10 – Central Cooling D3030.30 – Evaporative Air-Cooling D3030.70 – Decentralized Cooling
DIN276 |  | KG 434 – Kälteanlagen KG 475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Chiller

## Chimney
Chimney
Return to overview
General
A chimney is a flue for the evacuation of combustion gases from a combustion heat generation system (wood, oil, gas, etc.) generally arranged vertically. A chimney can be fully prefabricated (single or double-walled flue with integrated insulation) or built on site (exterior masonry + insulation + steel flue, terracotta refractory lining… on a case-by-case basis). The same chimney can contain one or more flues. A chimney can also comprise concentric ducts known as “suction ducts”, with one of the ducts providing fresh air for combustion and the other serving to evacuate the combustion gases.
Autres fiches pour conduit : sanitary/heating pipe, sanitary/heating pipe fitting, ventilation duct, ventilation duct connection, water collector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Whole chimney |  | IfcBuildingElementProxy.USERDEFINED[CHIMNEY] | [5 empty] | IfcChimney.NOTDEFINED |  | IfcChimney.NOTDEFINED
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Diameter |  |  | X | X | X | X
Architectural design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Diameter |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Diameter |  |  | X |  | X
Clash detection (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Diameter |  |  | X | X | X | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Acoustics (partial requirements)
Thickness of each layer |  |  |  | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ChimneyCommon.Status1 |  | Pset_ChimneyCommon.Status |  | Pset_ChimneyCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
LCA (Life Cycle Analysis)
Number of ducts |  |  |  |  | X |  | ePset_ChimneyCommon.NumberofDrafts1 |  | Pset_ChimneyCommon.NumberOfDrafts |  | Pset_ChimneyCommon.NumberOfDrafts
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Construction details |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B3020.10 – Roof Accessories B3060.50 – Vents and Hatches
DIN276 |  | KG 399 – Sonstiges zur KG390 (Sonstige Maßnahmen für Baukonstruktionen) KG 429 – Sonstiges zur KG420 (Wärmeversorgungsalagen)
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Column
Column
Return to overview
General
A column or a pillar (embedded in a wall) is a generally vertical (sometimes oblique) construction element serving to take concentrated loads - mainly compression but also horizontal - and to transmit them to the structural elements below.
Other sheets for linear structural elements : beam, linear structural member.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Column (isolated) |  | IfcColumn.COLUMN | [5 empty] | IfcColumn.COLUMN |  | IfcColumn.COLUMN
Pilaster (wall) |  | IfcColumn.USERDEFINED[PILASTER] | [5 empty] | IfcColumn.PILASTER |  | IfcColumn.PILASTER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Diameter | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Diameter |  |  |  | X | X
Section profile |  |  |  | X | X
Reservations |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X
2D documents (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Diameter | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Fire safety (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Architectural design (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Diameter | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Diameter |  |  | X |  | X
Section profile |  |  | X |  | X
Acoustics (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Clash detection (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Diameter | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Length | X |  | X | X | X | X
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Diameter | X |  | X | X | X | X
Section profile |  |  |  | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_ColumnCommon.Status1 |  | Pset_ColumnCommon.Status |  | Pset_ColumnCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_ColumnCommon.Status |  | Pset_ColumnCommon.Status |  | Pset_ColumnCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | Pset_ColumnCommon.LoadBearing |  | Pset_ColumnCommon.LoadBearing |  | Pset_ColumnCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_ColumnCommon.IsExternal |  | Pset_ColumnCommon.IsExternal |  | Pset_ColumnCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_ColumnCommon.FireRating |  | Pset_ColumnCommon.FireRating |  | Pset_ColumnCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Geotechnical study report | X |  | X | X | X | X
Stability report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1010.10 – Floor Structural Frame B1020.10 – Roof Structural Frame B3080.10 – Exterior Ceiling F1020.40 – Metal Building Systems
DIN276 |  | 333 – Aussenstützen 343 – Innenstützen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Curtain wall
Curtain wall
Return to overview
General
A curtain wall is a vertical (or almost vertical), partially or completely glazed wall, which closes the spaces of a building vertically, generally running outside and not between the floor slabs. This wall is composed of several elements:
- A load-bearing structure composed of profiles, all fixed to the slabs/walls of the building
- Glazed or opaque panels fixed to the structure (glued or clipped-in exterior glazing panels)
- Insulation and interior finish as appropriate
Other sheets for vertical walls and opening elements : wall, door, window.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Curtain wall |  | IfcCurtainWall.NOTDEFINED | [5 empty] | IfcCurtainWall.NOTDEFINED |  | IfcCurtainWall.NOTDEFINED
Canopy |  | IfcCurtainWall.NOTDEFINED | [5 empty] | IfcCurtainWall.NOTDEFINED |  | IfcCurtainWall.NOTDEFINED
Veranda |  | IfcCurtainWall.NOTDEFINED | [5 empty] | IfcCurtainWall.NOTDEFINED |  | IfcCurtainWall.NOTDEFINED
The components of an IfcCurtainWall are:
- Structure (mullions): IfcMember (IFC2x3 and IFC4) – MULLION
- Glazed/opaque panel: IfcPlate (IFC2x3 et IFC4) – CURTAIN_PANEL
- Opening panel: IfcWindow (see window)
- Door integrated in the curtain wall: IfcDoor (see door)
- Shading: IfcShadingDevice (IFC4) – JALOUSIE – SHUTTER – AWNING – USERDEFINED – NOTDEFINED
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Height |  |  | X
Thickness |  |  | X
Profiles, joinery and glazing |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
2D documents (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
Profiles, joinery and glazing |  |  | X | X | X | X
Heat loss calculation
Length | X |  | X | X
Height | X |  | X | X
Thickness |  |  | X | X
Reservations |  |  | X | X
Architectural design (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
Profiles, joinery and glazing |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Height |  |  | X |  | X
Thickness |  |  |  |  | X
Acoustics (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Profiles, joinery and glazing |  |  | X | X | X | X
Clash detection (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
Profiles, joinery and glazing |  |  | X | X | X | X
Rendering (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Profiles, joinery and glazing |  |  | X | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Profiles, joinery and glazing |  |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_CurtainWallCommon.Status1 |  | Pset_CurtainWallCommon.Status |  | Pset_CurtainWallCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external | X |  | X | X | X | X | Pset_CurtainWallCommon.IsExternal |  | Pset_CurtainWallCommon.IsExternal |  | Pset_CurtainWallCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CurtainWallCommon.FireRating |  | Pset_CurtainWallCommon.FireRating |  | Pset_CurtainWallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
LCA (Life Cycle Analysis)
Thermal transmittance |  |  | X |  | X |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance |  | Pset_CurtainWallCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Layout plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B2010.40 – Fabricated Exterior Walls Assemblies
DIN276 |  | 337 – Elementierte Außenwandkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Damper and register
Damper and register
Return to overview
General
A flap is an equipment item that allows the airflow through a duct to be closed off as needed (0 or 100%): fire-blocking flap at compartmentalisation level, … A damper is an equipment item that allows the airflow to be adjusted gradually, manually or with a motor. When the flow adjustment is integrated into the final element of the circuit (grille), this element is considered to be a vent with integrated flap/damper.
Other sheets for ventilation accessory elements: fan, air-to-air exchanger, air handling unit, vent, filter, silencer.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Hood |  | IfcDamperType.FUMEHOODEXHAUST | [5 empty] | IfcDamper.FUMEHOODEXHAUST |  | IfcDamper.FUMEHOODEXHAUST
Backdraft damper |  | IfcDamperType.BACKDRAFTDAMPER | [5 empty] | IfcDamper.BACKDRAFTDAMPER |  | IfcDamper.BACKDRAFTDAMPER
Fire damper |  | IfcDamperType.FIREDAMPER | [5 empty] | IfcDamper.FIREDAMPER |  | IfcDamper.FIREDAMPER
Smoke damper (chimney) |  | IfcDamperType.SMOKEDAMPER | [5 empty] | IfcDamper.SMOKEDAMPER |  | IfcDamper.SMOKEDAMPER
Smoke damper (fire) |  | IfcDamperType.FIRESMOKEDAMPER | [5 empty] | IfcDamper.FIRESMOKEDAMPER |  | IfcDamper.FIRESMOKEDAMPER
Balancing damper |  | IfcDamperType.BALANCINGDAMPER | [5 empty] | IfcDamper.BALANCINGDAMPER |  | IfcDamper.BALANCINGDAMPER
Motorised damper |  | IfcDamperType.CONTROLDAMPER | [5 empty] | IfcDamper.CONTROLDAMPER |  | IfcDamper.CONTROLDAMPER
Blast damper |  | IfcDamperType.BLASTDAMPER | [5 empty] | IfcDamper.BLASTDAMPER |  | IfcDamper.BLASTDAMPER
Pressure relief damper |  | IfcDamperType.RELIEFDAMPER | [5 empty] | IfcDamper.RELIEFDAMPER |  | IfcDamper.RELIEFDAMPER
Vacuum damper |  | IfcDamperType.RELIEFDAMPER | [5 empty] | IfcDamper.RELIEFDAMPER |  | IfcDamper.RELIEFDAMPER
When the flap or damper is integrated into the vent, use: IFcFlowterminal-REGISTER (IFC 2x3) and IfcAirTerminal-REGISTER (IFC 4), see vent
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_DamperTypeCommon.Status1 |  | Pset_DamperTypeCommon.Status |  | Pset_DamperTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_DamperTypeCommon.FireRating |  | Pset_DamperTypeCommon.FireRating |  | Pset_DamperTypeCommon.FireRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3050.50 – HVAC Air Distribution D4030.50 – Breathing air Replenishment Systems C1090.50 – Fireplace and Stoves
DIN276 |  | KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Damper and register

## Data device
Data device
Return to overview
General
A data device is a device that serves to exchange computer data. It generally requires a power supply and can be fixed or movable. Devices intended primarily for Audio and/or Video are not included here.
Other data sheet relating to electrical appliances: audiovisual device, electric appliance.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Mobile phone antenna |  | IfcElectricApplianceType.USERDEFINED[ANTENNA] | [5 empty] | IfcCommunicationsAppliance.ANTENNA |  | IfcCommunicationsAppliance.ANTENNA
Mobile phone relay |  | IfcElectricApplianceType.USERDEFINED[ANTENNA] | [5 empty] | IfcCommunicationsAppliance.ANTENNA |  | IfcCommunicationsAppliance.ANTENNA
Home automation gateway |  | IfcElectricApplianceType.USERDEFINED[GATEWAY] | [5 empty] | IfcCommunicationsAppliance.GATEWAY |  | IfcCommunicationsAppliance.GATEWAY
Antenna |  | IfcElectricApplianceType.USERDEFINED[ANTENNA] | [5 empty] | IfcCommunicationsAppliance.ANTENNA |  | IfcCommunicationsAppliance.ANTENNA
Printer |  | IfcElectricApplianceType.PRINTER | [5 empty] | IfcCommunicationsAppliance.PRINTER |  | IfcCommunicationsAppliance.PRINTER
Computer |  | IfcElectricApplianceType.COMPUTER | [5 empty] | IfcCommunicationsAppliance.COMPUTER |  | IfcCommunicationsAppliance.COMPUTER
Server |  | IfcElectricApplianceType.COMPUTER | [5 empty] | IfcCommunicationsAppliance.COMPUTER |  | IfcCommunicationsAppliance.COMPUTER
Network hub |  | IfcElectricApplianceType.USERDEFINED[NETWORKHUB] | [5 empty] | IfcCommunicationsAppliance.NETWORKHUB |  | IfcCommunicationsAppliance.NETWORKHUB
Data switch |  | IfcElectricApplianceType.USERDEFINED[NETWORKHUB] | [5 empty] | IfcCommunicationsAppliance.NETWORKHUB |  | IfcCommunicationsAppliance.NETWORKHUB
Fax |  | IfcElectricApplianceType.USERDEFINED[FAX] | [5 empty] | IfcCommunicationsAppliance.FAX |  | IfcCommunicationsAppliance.FAX
Internet modem |  | IfcElectricApplianceType.USERDEFINED[MODEM] | [5 empty] | IfcCommunicationsAppliance.MODEM |  | IfcCommunicationsAppliance.MODEM
Network accessory (firewall, network load balancer,etc.) |  | IfcElectricApplianceType.USERDEFINED[NETWORKAPPLIANCE] | [5 empty] | IfcCommunicationsAppliance.NETWORKAPPLIANCE |  | IfcCommunicationsAppliance.NETWORKAPPLIANCE
Repeater (Wifi, gsm,etc.) |  | IfcElectricApplianceType.USERDEFINED[REPEATER] | [5 empty] | IfcCommunicationsAppliance.REPEATER |  | IfcCommunicationsAppliance.REPEATER
Scanner |  | IfcElectricApplianceType.SCANNER | [5 empty] | IfcCommunicationsAppliance.SCANNER |  | IfcCommunicationsAppliance.SCANNER
Router (wifi access point,etc.) |  | IfcElectricApplianceType.USERDEFINED[ROUTER] | [5 empty] | IfcCommunicationsAppliance.ROUTER |  | IfcCommunicationsAppliance.ROUTER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ElectricApplianceTypeCommon.Status1 |  | Pset_CommunicationsApplianceTypeCommon.Status |  | Pset_CommunicationsApplianceTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_ElectricApplianceTypeCommon.Status1 |  | Pset_CommunicationsApplianceTypeCommon.Status |  | Pset_CommunicationsApplianceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D6010 – Data Communications
DIN276 |  | KG455 – Audiovisuelle Medien- und Antennenanlagen KG457 – Datenüberstragungsnetze (Kommunikations-, sicherheits- und informationstechnische Anlagen) KG485 – Datenübertragungsnetze (Gebäude- und Anlagenautomation)
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Data device

## Deep foundation
Deep foundation
Return to overview
General
A pile is a deep foundation that transmits the loads of a structure to the deeper layers of the ground. The load is transmitted by lateral friction and/or at the tip. This type of structure is used when the loads to be transmitted to the ground are too great to work with direct foundations and/or when the bearing capacity of the upper layers of the ground is too low.
Other sheets for foundations/deep foundations : foundation beam, caisson foundation
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
False wells |  | IfcPile.SUPPORT | [5 empty] | IfcPile.SUPPORT |  | IfcPile.SUPPORT
Driven pile |  | IfcPile.USERDEFINED[DRIVEN] | [5 empty] | IfcPile.DRIVEN |  | IfcPile.DRIVEN
Bored pile |  | IfcPile.USERDEFINED[BORED] | [5 empty] | IfcPile.BORED |  | IfcPile.BORED
Jet grouting pile |  | IfcPile.USERDEFINED[JETGROUTING] | [5 empty] | IfcPile.JETGROUTING |  | IfcPile.JETGROUTING
Vibrated pile |  | IfcPile.USERDEFINED[DRIVEN] | [5 empty] | IfcPile.DRIVEN |  | IfcPile.DRIVEN
MV pile |  | IfcPile.USERDEFINED[DRIVEN] | [5 empty] | IfcPile.DRIVEN |  | IfcPile.DRIVEN
CFA pile |  | IfcPile.USERDEFINED[BORED] | [5 empty] | IfcPile.BORED |  | IfcPile.BORED
Screw pile |  | IfcPile.USERDEFINED[SCREW_PILE] | [5 empty] | IfcPile.USERDEFINED[SCREW_PILE] |  | IfcPile.USERDEFINED[SCREW_PILE]
Pipe pile |  | IfcPile.USERDEFINED[DRIVEN] | [5 empty] | IfcPile.DRIVEN |  | IfcPile.DRIVEN
Soil mix |  | IfcPile.USERDEFINED[SOILMIX] | [5 empty] | IfcPile.USERDEFINED[SOILMIX] |  | IfcPile.USERDEFINED[SOILMIX]
Micropile |  | IfcPile.USERDEFINED[BORED] | [5 empty] | IfcPile.BORED |  | IfcPile.BORED
Stone columns |  | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | [5 empty] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] |  | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS]
Rigid inclusions |  | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] | [5 empty] | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS] |  | IfcPile.USERDEFINED[GROUND_IMPROVEMENTS]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
2D documents (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Clash detection (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Diameter |  |  |  | X | X
Section profile |  |  |  | X | X
Reservations |  |  |  | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Fire safety (partial requirements)
Accessories and specific elements |  |  |  | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_PileCommon.Status1 |  | Pset_PileCommon.Status |  | Pset_PileCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | ePset_PileCommon.Status1 |  | Pset_PileCommon.Status |  | Pset_PileCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | ePset_PileCommon.LoadBearing1 |  | Pset_PileCommon.LoadBearing |  | Pset_PileCommon.LoadBearing
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Geotechnical study report | X |  | X | X | X | X
Stability report |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A1020.10 – Driven Piles A1020.15 – Bored Piles
DIN276 |  | 323 – Tiefgründungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Door
Door
Return to overview
General
A door is a construction element that serves mainly to provide controlled access to persons and goods. It mainly takes the form of vertical openings but also includes horizontal openings (hatches). A door generally consists of a frame (fixed part) and one or more panels (moving parts), plus accessories such as hinges and pivoting, sliding or folding hardware. It can also incorporate solar or blackout protection.
Other data sheets for openings and elements with openings as components : window, curtain wall.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Door |  | IfcDoor | [5 empty] | IfcDoor |  | IfcDoor
Gate |  | IfcDoor | [5 empty] | IfcDoor.GATE |  | IfcDoor.GATE
Wicket gate |  | IfcDoor | [5 empty] | IfcDoor.GATE |  | IfcDoor.GATE
Inspection hatch |  | IfcDoor | [5 empty] | IfcDoor.TRAPDOOR |  | IfcDoor.TRAPDOOR
Access hatch |  | IfcDoor | [5 empty] | IfcDoor.TRAPDOOR |  | IfcDoor.TRAPDOOR
Garage door |  | IfcDoor | [5 empty] | IfcDoor.DOOR |  | IfcDoor.DOOR
Arm barrier |  | IfcDoor | [5 empty] | IfcDoor.GATE |  | IfcDoor.GATE
The components of an IfcDoor are:
- Sun protection integrated or not in the IfcDoor: IfcShadingDevice (IFC4) – JALOUSIE – SHUTTER – AWNING – USERDEFINED – NOTDEFINED
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Access management (partial requirements)
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Door frame (fixed) - dimensions |  |  |  | X | X | X
Door panel (mobile) - dimensions |  |  |  | X | X | X
Operation of the door |  |  |  | X | X | X
Building permit (partial requirements)
Width |  |  | X
Height |  |  | X
Door frame (fixed) - dimensions |  |  | X
Door panel (mobile) - dimensions |  |  | X
Operation of the door |  |  | X
Threshold - dimensions |  |  | X
Stool - dimensions |  |  | X
Shading device box - dimensions |  |  | X
PEB (partial requirements)
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
2D documents (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
Operation of the door | X |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Heat loss calculation
Width | X |  | X | X
Height | X |  | X | X
Architectural design (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
Operation of the door | X |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Handicap accessibility (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
Operation of the door | X |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Width |  |  | X |  | X
Height |  |  | X |  | X
Door frame (fixed) - dimensions |  |  | X |  | X
Door panel (mobile) - dimensions |  |  | X |  | X
Maintenance (partial requirements)
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Representative modelling (manufacturer element) |  |  |  |  | X | X
Door frame (fixed) - dimensions |  |  |  |  | X | X
Door panel (mobile) - dimensions |  |  |  |  | X | X
Operation of the door |  |  |  |  | X | X
Threshold - dimensions |  |  |  |  | X | X
Stool - dimensions |  |  |  |  | X | X
Shading device box - dimensions |  |  |  |  | X | X
Acoustics (partial requirements)
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Clash detection (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
Operation of the door | X |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Intrusion and surveillance (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  |  | X | X | X
Door panel (mobile) - dimensions |  |  |  | X | X | X
Operation of the door | X |  | X | X | X | X
Rendering (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Door frame (fixed) - dimensions |  |  | X | X | X | X
Door panel (mobile) - dimensions |  |  | X | X | X | X
Operation of the door | X |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_DoorCommon.Status1 |  | Pset_DoorCommon.Status |  | Pset_DoorCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external | X |  | X | X | X | X | Pset_DoorCommon.IsExternal |  | Pset_DoorCommon.IsExternal |  | Pset_DoorCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_DoorCommon.FireRating |  | Pset_DoorCommon.FireRating |  | Pset_DoorCommon.FireRating
Is emergency exit |  |  | X | X | X | X | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Operation type | X |  | X | X | X | X | IfcDoorStyle.OperationType |  | IfcElementAttributes.OperationType |  | IfcElementAttributes.OperationType
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Has access control |  |  |  | X | X | X | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2
Is mobile shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_DoorCommon.FireRating |  | Pset_DoorCommon.FireRating |  | Pset_DoorCommon.FireRating
Is emergency exit |  |  |  |  | X | X | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit
Thermal transmittance |  |  |  |  | X | X | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance
Acoustic resistance |  |  |  |  | X | X | Pset_DoorCommon.AcousticRating |  | Pset_DoorCommon.AcousticRating |  | Pset_DoorCommon.AcousticRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Flammability rating |  |  |  |  | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Solar transmission of glazing |  |  |  |  | X | X | Pset_DoorWindowGlazingType.SolarHeatGainTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance
Glass layers |  |  |  |  | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Glazing area fraction |  |  |  |  | X | X | ePset_DoorWindowGlazingType.GlazingAreaFraction1 |  | Pset_DoorCommon.GlazingAreaFraction |  | Pset_DoorCommon.GlazingAreaFraction
Type of blackout device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Is mobile shading device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Bulletproof |  |  |  |  | X | X | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2
Access management (partial requirements)
Is emergency exit |  |  |  | X | X | X | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit
Operation type |  |  |  | X | X | X | IfcDoorStyle.OperationType |  | IfcElementAttributes.OperationType |  | IfcElementAttributes.OperationType
Has motorized opening |  |  |  | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Has access control |  |  |  | X | X | X | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2
Is mobile shading device |  |  |  | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  |  | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Passage width |  |  |  | X | X | X | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2
Building permit (partial requirements)
Is emergency exit |  |  | X |  |  |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit
Thermal transmittance |  |  | X |  |  |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance
Is handicap accessible |  |  | X |  |  |  | Pset_DoorCommon.HandicapAccessible |  | Pset_DoorCommon.HandicapAccessible |  | Pset_DoorCommon.HandicapAccessible
Glazing area fraction |  |  | X |  |  |  | ePset_DoorWindowGlazingType.GlazingAreaFraction1 |  | Pset_DoorCommon.GlazingAreaFraction |  | Pset_DoorCommon.GlazingAreaFraction
Intrusion and surveillance (partial requirements)
Is emergency exit |  |  | X | X | X | X | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit |  | Pset_DoorCommon.FireExit
Has access control |  |  |  | X | X | X | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2
Bulletproof |  |  |  | X | X | X | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2
Security rating |  |  |  | X | X | X | Pset_DoorCommon.SecurityRating |  | Pset_DoorCommon.SecurityRating |  | Pset_DoorCommon.SecurityRating
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Solar transmission of glazing |  |  | X | X | X | X | Pset_DoorWindowGlazingType.SolarHeatGainTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance
Glass layers |  |  | X | X | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Type of blackout device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Is mobile shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Ventilation gap surface |  |  | X | X | X | X | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
LCA (Life Cycle Analysis)
Thermal transmittance |  |  | X |  | X |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance |  | Pset_DoorCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_DoorCommon.AcousticRating |  | Pset_DoorCommon.AcousticRating |  | Pset_DoorCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Glass layers |  |  | X | X | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Handicap accessibility (partial requirements)
Is handicap accessible | X |  | X | X | X | X | Pset_DoorCommon.HandicapAccessible |  | Pset_DoorCommon.HandicapAccessible |  | Pset_DoorCommon.HandicapAccessible
Operation type | X |  | X | X | X | X | IfcDoorStyle.OperationType |  | IfcElementAttributes.OperationType |  | IfcElementAttributes.OperationType
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Passage width |  |  | X | X | X | X | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2
Architectural design (partial requirements)
Operation type | X |  | X | X | X | X | IfcDoorStyle.OperationType |  | IfcElementAttributes.OperationType |  | IfcElementAttributes.OperationType
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Has access control |  |  |  | X | X | X | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2
Type of blackout device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Has external sill |  |  |  | X | X | X | Pset_DoorWindowGlazingType.HasSillExternal |  | Pset_WindowCommon.HasSillExternal |  | Pset_WindowCommon.HasSillExternal
Has internal sill |  |  |  | X | X | X | Pset_DoorWindowGlazingType.HasSillInternal |  | Pset_WindowCommon.HasSillInternal |  | Pset_WindowCommon.HasSillInternal
Electrical design (partial requirements)
Has access control |  |  |  | X | X | X | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2 |  | BIMids_Door.AccessControl2
Rendering (partial requirements)
Passage width |  |  | X | X | X | X | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Shading principle |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Plans and diagrams
Construction details |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Tables
List of doors |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Operation and technical sheets
Communication protocol |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B2050 – Exterior Doors and Grilles B3060.50 – Vents and Hatches C1030 – Interior DoorsC1040 - Interior Grilles and Gates C1090.35 – Wall and Door Protection
DIN276 |  | 334 – Außenwandöffnungen 344 – Innenwandöffnungen 352 – Deckenöffnungen 362 – Dachöffnungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Electric appliance
Electric appliance
Return to overview
General
An electrical appliance covers devices, both fixed and movable, intended to run on electricity, excluding communication, multimedia, permanent and/or fixed heating and cooling appliances.
Other data sheet relating to electrical devices: data device, audiovisual device.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Freezer |  | IfcElectricApplianceType.FREEZER | [5 empty] | IfcElectricAppliance.FREEZER |  | IfcElectricAppliance.FREEZER
Combined refrigerator |  | IfcElectricApplianceType.FRIDGE_FREEZER | [5 empty] | IfcElectricAppliance.FRIDGE_FREEZER |  | IfcElectricAppliance.FRIDGE_FREEZER
Fridge |  | IfcElectricApplianceType.REFRIGERATOR | [5 empty] | IfcElectricAppliance.REFRIGERATOR |  | IfcElectricAppliance.REFRIGERATOR
Refrigerator |  | IfcElectricApplianceType.REFRIGERATOR | [5 empty] | IfcElectricAppliance.REFRIGERATOR |  | IfcElectricAppliance.REFRIGERATOR
Dishwasher |  | IfcElectricApplianceType.DISHWASHER | [5 empty] | IfcElectricAppliance.DISHWASHER |  | IfcElectricAppliance.DISHWASHER
Microwave |  | IfcElectricApplianceType.MICROWAVE | [5 empty] | IfcElectricAppliance.MICROWAVE |  | IfcElectricAppliance.MICROWAVE
Photocopier |  | IfcElectricApplianceType.PHOTOCOPIER | [5 empty] | IfcElectricAppliance.PHOTOCOPIER |  | IfcElectricAppliance.PHOTOCOPIER
Hob |  | IfcElectricApplianceType.ELECTRICCOOKER | [5 empty] | IfcElectricAppliance.ELECTRICCOOKER |  | IfcElectricAppliance.ELECTRICCOOKER
Cooking hob |  | IfcElectricApplianceType.ELECTRICCOOKER | [5 empty] | IfcElectricAppliance.ELECTRICCOOKER |  | IfcElectricAppliance.ELECTRICCOOKER
Electric cooker |  | IfcElectricApplianceType.ELECTRICCOOKER | [5 empty] | IfcElectricAppliance.ELECTRICCOOKER |  | IfcElectricAppliance.ELECTRICCOOKER
Kitchen robot |  | IfcElectricApplianceType.USERDEFINED[KITCHENMACHINE] | [5 empty] | IfcElectricAppliance.KITCHENMACHINE |  | IfcElectricAppliance.KITCHENMACHINE
Kitchen machine |  | IfcElectricApplianceType.USERDEFINED[KITCHENMACHINE] | [5 empty] | IfcElectricAppliance.KITCHENMACHINE |  | IfcElectricAppliance.KITCHENMACHINE
Fixed hair dryer |  | IfcElectricApplianceType.USERDEFINED[HAIRDRYER] | [5 empty] | IfcElectricAppliance.USERDEFINED[HAIRDRYER] |  | IfcElectricAppliance.USERDEFINED[HAIRDRYER]
Hand dryer |  | IfcElectricApplianceType.HANDDRYER | [5 empty] | IfcElectricAppliance.HANDDRYER |  | IfcElectricAppliance.HANDDRYER
Oven |  | IfcElectricApplianceType.USERDEFINED[OVEN] | [5 empty] | IfcElectricAppliance.USERDEFINED[OVEN] |  | IfcElectricAppliance.USERDEFINED[OVEN]
Washing machine |  | IfcElectricApplianceType.WASHINGMACHINE | [5 empty] | IfcElectricAppliance.WASHINGMACHINE |  | IfcElectricAppliance.WASHINGMACHINE
Tumble dryer |  | IfcElectricApplianceType.TUMBLEDRYER | [5 empty] | IfcElectricAppliance.TUMBLEDRYER |  | IfcElectricAppliance.TUMBLEDRYER
Cash dispenser |  | IfcElectricApplianceType.USERDEFINED[ATM] | [5 empty] | IfcElectricAppliance.USERDEFINED[ATM] |  | IfcElectricAppliance.USERDEFINED[ATM]
ATM |  | IfcElectricApplianceType.USERDEFINED[ATM] | [5 empty] | IfcElectricAppliance.USERDEFINED[ATM] |  | IfcElectricAppliance.USERDEFINED[ATM]
Water cooler |  | IfcElectricApplianceType.WATERCOOLER | [5 empty] | IfcElectricAppliance.FREESTANDINGWATERCOOLER |  | IfcElectricAppliance.FREESTANDINGWATERCOOLER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ElectricApplianceTypeCommon.Status1 |  | Pset_ElectricApplianceTypeCommon.Status |  | Pset_ElectricApplianceTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_ElectricApplianceTypeCommon.Status1 |  | Pset_ElectricApplianceTypeCommon.Status |  | Pset_ElectricApplianceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
Current |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent
Electrical design (partial requirements)
Current |  |  |  | X | X | X | Pset_ElectricalDeviceCommon.NominalCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5030.50 – Wiring Devices
DIN276 |  | KG449 – Sonstige zur Elektrische Anlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electric appliance

## Electrical generator
Electrical generator
Return to overview
General
An electricity generator is a device that converts kinetic energy into electricity, consisting of a fuel-powered motor or turbine that drives an electric generator. In certain cases it can also produce heat (co-generation).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Cogenerator |  | IfcElectricGeneratorType.USERDEFINED[CHP] | [5 empty] | IfcElectricGenerator.CHP |  | IfcElectricGenerator.CHP
Generator set |  | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | [5 empty] | IfcElectricGenerator.ENGINEGENERATOR |  | IfcElectricGenerator.ENGINEGENERATOR
Safety electric generator |  | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | [5 empty] | IfcElectricGenerator.ENGINEGENERATOR |  | IfcElectricGenerator.ENGINEGENERATOR
Replacement generator set (operation) |  | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | [5 empty] | IfcElectricGenerator.ENGINEGENERATOR |  | IfcElectricGenerator.ENGINEGENERATOR
Production generator set |  | IfcElectricGeneratorType.USERDEFINED[ENGINGENERATOR] | [5 empty] | IfcElectricGenerator.ENGINEGENERATOR |  | IfcElectricGenerator.ENGINEGENERATOR
Electric generator (without combustion engine) |  | IfcElectricGeneratorType.USERDEFINED[STANDALONE] | [5 empty] | IfcElectricGenerator.STANDALONE |  | IfcElectricGenerator.STANDALONE
It is possible to decompose the electric generator into several IFC entities:
- The combustion motor: IfcEngine (IFC4) - EXTERNALCOMBUSTION - INTERNALCOMBUSTION
- The generator: see above under "electric generator (without motor)".
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Electrical design (partial requirements)
Symbol | X
Length |  |  | X | X | X
Width |  |  | X | X | X
Height |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_ElectricGeneratorTypeCommon.Status |  | Pset_ElectricGeneratorTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Performance |  |  |  |  | X | X | Pset_ElectricGeneratorTypeCommon.ElectricGeneratorEfficiency |  | Pset_ElectricGeneratorTypeCommon.ElectricGeneratorEfficiency |  | Pset_ElectricGeneratorTypeCommon.ElectricGeneratorEfficiency
Maximum output power |  |  |  |  | X | X | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput |  | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput |  | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput
Electrical design (partial requirements)
Maximum output power |  |  |  | X | X | X | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput |  | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput |  | Pset_ElectricGeneratorTypeCommon.MaximumPowerOutput
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5010.90 – Facility Power Generation Supplementary Components
DIN276 |  | KG 442 – Eigenstromversorgungsanlagen KG 475 – prozesswärme-, Kälte- und -Luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Electrical outlet
Electrical outlet
Return to overview
General
A switch is an accessory belonging to an electrical distribution network that makes it possible to control and modulate the intensity of the electrical current downstream. A switch makes it possible to control a power current, a communication or audio-visual signal, or any other type of flow.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Electrical outlet (single-phase, three-phase .,etc.) |  | IfcOutletType.POWEROUTLET | [5 empty] | IfcOutlet.POWEROUTLET |  | IfcOutlet.POWEROUTLET
Data socket (RJ45,etc.) |  | IfcOutletType.USERDEFINED[DATAOUTLET] | [5 empty] | IfcOutlet.DATAOUTLET |  | IfcOutlet.DATAOUTLET
Telephone socket (RJ11,etc.) |  | IfcOutletType.USERDEFINED[TELEPHONEOUTLET] | [5 empty] | IfcOutlet.TELEPHONEOUTLET |  | IfcOutlet.TELEPHONEOUTLET
Audiovisual socket (RCA, mini-jack, jack, XlR, mini-DIN, VGA SubD15, DVI, HDMI, DP, coaxial antenna and TV,etc.) |  | IfcOutletType.AUDIOVISUALOUTLET | [5 empty] | IfcOutlet.AUDIOVISUALOUTLET |  | IfcOutlet.AUDIOVISUALOUTLET
Car charging station |  | IfcOutletType.USERDEFINED[CHARGING_STATION] | [5 empty] | IfcOutlet.USERDEFINED[CHARGING_STATION] |  | IfcOutlet.USERDEFINED[CHARGING_STATION]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Electrical design (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X
Width |  |  |  |  | X
Thickness |  |  |  |  | X
Maintenance (partial requirements)
Symbol |  |  |  |  | X | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Thickness | [5 empty] | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_OutletTypeCommon.Status1 |  | Pset_OutletTypeCommon.Status |  | Pset_OutletTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Recessed |  |  |  |  | X | X | ePset_OutletTypeCommon.MountingType1 |  | ePset_OutletTypeCommon.MountingType1 |  | ePset_OutletTypeCommon.MountingType1
Type connection |  |  |  |  | X | X | Pset_OutletTypeCommon.IsPluggableOutlet |  | Pset_OutletTypeCommon.IsPluggableOutlet |  | Pset_OutletTypeCommon.IsPluggableOutlet
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
Current |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent
Electrical design (partial requirements)
Recessed |  |  |  | X | X | X | ePset_OutletTypeCommon.MountingType1 |  | ePset_OutletTypeCommon.MountingType1 |  | ePset_OutletTypeCommon.MountingType1
Type connection |  |  |  | X | X | X | Pset_OutletTypeCommon.IsPluggableOutlet |  | Pset_OutletTypeCommon.IsPluggableOutlet |  | Pset_OutletTypeCommon.IsPluggableOutlet
Current |  |  |  | X | X | X | Pset_ElectricalDeviceCommon.NominalCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent |  | Pset_ElectricalDeviceCommon.RatedCurrent
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5030.50 – Wiring Devices D6010.10 – Data Communications Network Equipment D6030.10 – Audio-Video Systems
DIN276 |  | KG 444 – Niederspannungsinstallionsanlagen KG 451 – telekommunikationsanlagen KG 455 – Audiovisuelle Medien- und Antennenanlegen KG 457 – datenübertragungsnetze
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electrical outlet

## Electrical panel
Electrical panel
Return to overview
General
An electrical panel is a box through which electrical power passes and is distributed to the various circuits. It can contain safety and protection devices (circuit breaker, differential), energy metering, circuit management and control (relays, dimmers, home automation control module, etc.).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Electric consumer unit |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.CONSUMERUNIT |  | IfcElectricDistributionBoard.CONSUMERUNIT
Electric switchboard |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.SWITCHBOARD |  | IfcElectricDistributionBoard.SWITCHBOARD
Electric distribution board |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.DISTRIBUTIONBOARD |  | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Main low voltage distribution board |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.DISTRIBUTIONBOARD |  | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Temporary electrical panel |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.DISTRIBUTIONBOARD |  | IfcElectricDistributionBoard.DISTRIBUTIONBOARD
Data board |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] |  | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Data rack |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] |  | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Server rack |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] |  | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Server cabinet |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] |  | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
Wiring closet |  | IfcElectricDistributionPoint | [5 empty] | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD] |  | IfcElectricDistributionBoard.USERDEFINED[DISPATCHINGBOARD]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Symbol |  |  | X
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ElectricDistributionPointTypeCommon.Status1 |  | Pset_ElectricDistributionBoardTypeCommon.Status |  | Pset_ElectricDistributionBoardTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.10 – Electrical Service D5020.30 – Power Distribution
DIN276 |  | KG 441 – Hoch- und Mittelspannungsanlagen KG 444 – Niederspannungsinstallationsanlagen KG 451 – Telekommunikationsanlagen KG 475 – Datenübertragungsnetze KG 482 – Schaltschranke, automationsschwerpunkte
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electrical panel

## Electrical protection equipment
Electrical protection equipment
Return to overview
General
Electrical protective equipment serves to automatically cut an electrical circuit when a limit condition is reached: Excessive current due to overload or short-circuit (circuit breaker, fuse…), loss of current (differential), overvoltage (Varistor)… Some accessories are also provided for manual actions with a view to isolating certain circuits, for example in order to work on this circuit.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fuse |  | IfcProtectiveDeviceType.FUSEDISCONNECTOR | [5 empty] | IfcProtectiveDevice.FUSEDISCONNECTOR |  | IfcProtectiveDevice.FUSEDISCONNECTOR
Main circuit breaker |  | IfcProtectiveDeviceType.CIRCUITBREAKER | [5 empty] | IfcProtectiveDevice.CIRCUITBREAKER |  | IfcProtectiveDevice.CIRCUITBREAKER
Circuit breaker |  | IfcProtectiveDeviceType.CIRCUITBREAKER | [5 empty] | IfcProtectiveDevice.CIRCUITBREAKER |  | IfcProtectiveDevice.CIRCUITBREAKER
Disconnecting switch |  | IfcProtectiveDeviceType.CIRCUITBREAKER | [5 empty] | IfcProtectiveDevice.CIRCUITBREAKER |  | IfcProtectiveDevice.CIRCUITBREAKER
Differential circuit breaker |  | IfcProtectiveDeviceType.RESIDUALCURRENTCIRCUITBREAKER | [5 empty] | IfcProtectiveDevice.RESIDUALCURRENTCIRCUITBREAKER |  | IfcProtectiveDevice.RESIDUALCURRENTCIRCUITBREAKER
Earth leakage circuit breaker |  | IfcProtectiveDeviceType.USERDEFINED[EARTHLEAKAGECIRCUITBREAKER] | [5 empty] | IfcProtectiveDevice.EARTHLEAKAGECIRCUITBREAKER |  | IfcProtectiveDevice.EARTHLEAKAGECIRCUITBREAKER
Earthing switch |  | IfcProtectiveDeviceType.USERDEFINED[EARTHINGSWITCH] | [5 empty] | IfcProtectiveDevice.EARTHINGSWITCH |  | IfcProtectiveDevice.EARTHINGSWITCH
Surge protector |  | IfcProtectiveDeviceType.VARISTOR | [5 empty] | IfcProtectiveDevice.VARISTOR |  | IfcProtectiveDevice.VARISTOR
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Thickness | [5 empty] | X
Electrical design (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Thickness |  |  |  | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_ProtectiveDeviceTypeCommon.Status1 |  | Pset_ProtectiveDeviceTypeCommon.Status |  | Pset_ProtectiveDeviceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.10 – Electrical Service D5080.10 – Lightning Protection G4010.50 – Electrical Switchgear and Protection Devices
DIN276 |  | KG 444 – Niederspannungsinstallationsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electrical protection equipment

## Electrical switch
Electrical switch
Return to overview
General
A switch is an accessory belonging to an electrical distribution network that makes it possible to control and modulate the intensity of the electrical current downstream. A switch makes it possible to control a power current, a communication or audio-visual signal, or any other type of flow.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Single pole switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Single-pole two-way switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Single-pole pull switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Double-pole switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Two-Pole Two-Way Switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Three-pole switch |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Changeover switch |  | IfcSwitchingDeviceType.TOGGLESWITCH | [5 empty] | IfcSwitchingDevice.TOGGLESWITCH |  | IfcSwitchingDevice.TOGGLESWITCH
Timer |  | IfcSwitchingDeviceType.USERDEFINED[TIMER] | [5 empty] | IfcSwitchingDevice.USERDEFINED[TIMER] |  | IfcSwitchingDevice.USERDEFINED[TIMER]
Push button |  | IfcSwitchingDeviceType.CONTACTOR | [5 empty] | IfcSwitchingDevice.CONTACTOR |  | IfcSwitchingDevice.CONTACTOR
Pulse switch (door closing) |  | IfcSwitchingDeviceType.STARTER | [5 empty] | IfcSwitchingDevice.STARTER |  | IfcSwitchingDevice.STARTER
Inverter |  | IfcSwitchingDeviceType.USERDEFINED[DIMMER_SWITCH] | [5 empty] | IfcSwitchingDevice.DIMMERSWITCH |  | IfcSwitchingDevice.DIMMERSWITCH
Dimmer switch |  | IfcSwitchingDeviceType.USERDEFINED[DIMMER_SWITCH] | [5 empty] | IfcSwitchingDevice.DIMMERSWITCH |  | IfcSwitchingDevice.DIMMERSWITCH
Patient call button |  | IfcSwitchingDeviceType.STARTER | [5 empty] | IfcSwitchingDevice.STARTER |  | IfcSwitchingDevice.STARTER
Foot switch for switching control |  | IfcSwitchingDeviceType.TOGGLESWITCH | [5 empty] | IfcSwitchingDevice.TOGGLESWITCH |  | IfcSwitchingDevice.TOGGLESWITCH
AV system port switch |  | IfcSwitchingDeviceType.USERDEFINED[SELECTORSWITCH] | [5 empty] | IfcSwitchingDevice.SELECTORSWITCH |  | IfcSwitchingDevice.SELECTORSWITCH
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Electrical design (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X
Width |  |  |  |  | X
Thickness |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Thickness | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_SwitchingDeviceTypeCommon.Status1 |  | Pset_SwitchingDeviceTypeCommon.Status |  | Pset_SwitchingDeviceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Switch function |  |  |  |  | X | X | Pset_SwitchingDeviceTypeCommon.SwitchFunction |  | Pset_SwitchingDeviceTypeCommon.SwitchFunction |  | Pset_SwitchingDeviceTypeCommon.SwitchFunction
Number of buttons |  |  |  |  | X | X | Pset_SwitchingDeviceTypeCommon.NumberOfGangs |  | Pset_SwitchingDeviceTypeCommon.NumberOfGangs |  | Pset_SwitchingDeviceTypeCommon.NumberOfGangs
Light switch |  |  |  |  | X | X | ePset_SwitchingDeviceTypeCommon.IsIlluminated1 |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated
Electrical design (partial requirements)
Switch function |  |  |  |  | X | X | Pset_SwitchingDeviceTypeCommon.SwitchFunction |  | Pset_SwitchingDeviceTypeCommon.SwitchFunction |  | Pset_SwitchingDeviceTypeCommon.SwitchFunction
Number of buttons |  |  |  |  | X | X | Pset_SwitchingDeviceTypeCommon.NumberOfGangs |  | Pset_SwitchingDeviceTypeCommon.NumberOfGangs |  | Pset_SwitchingDeviceTypeCommon.NumberOfGangs
Light switch |  |  |  | X | X | X | ePset_SwitchingDeviceTypeCommon.IsIlluminated1 |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated
Handicap accessibility (partial requirements)
Light switch |  |  |  | X | X | X | ePset_SwitchingDeviceTypeCommon.IsIlluminated1 |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated |  | Pset_SwitchingDeviceTypeCommon.IsIlluminated
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.10 – Electrical Service D5030.50 – Wiring Devices D5040.10 Lighting control
DIN276 |  | KG 444 – Niederspannungsinstallationsanlagen KG 451 – Telekommunikationsanlagen KG 457 – Datenübertragungsnetze
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electrical switch

## Electrical transformer
Electrical transformer
Return to overview
General
A transformer is an electrical component which uses induction to modify the voltage and the intensity of the current between 2 distinct electrical circuits. This data sheet covers only power transformers. Additional components built into the transformer can change the frequency and type (AC-DC) of the current. Some transformers serve to protect against electrocution.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Voltage transformer |  | IfcTransformerType.VOLTAGE | [5 empty] | IfcTransformer.VOLTAGE |  | IfcTransformer.VOLTAGE
Isolation transformer |  | IfcTransformerType.USERDEFINED[ISOLATIONTRANSFORMER] | [5 empty] | IfcTransformer.USERDEFINED[ISOLATIONTRANSFORMER] |  | IfcTransformer.USERDEFINED[ISOLATIONTRANSFORMER]
Measuring transformer |  | IfcTransformerType.CURRENT | [5 empty] | IfcTransformer.CURRENT |  | IfcTransformer.CURRENT
Inverter transformer |  | IfcTransformerType.USERDEFINED[INVERTER] | [5 empty] | IfcTransformer.INVERTER |  | IfcTransformer.INVERTER
Inverter |  | IfcTransformerType.USERDEFINED[INVERTER] | [5 empty] | IfcTransformer.INVERTER |  | IfcTransformer.INVERTER
Transformer rectifier |  | IfcTransformerType.USERDEFINED[RECTIFIER] | [5 empty] | IfcTransformer.RECTIFIER |  | IfcTransformer.RECTIFIER
Frequency inverter for motors |  | IfcTransformerType.FREQUENCY | [5 empty] | IfcTransformer.FREQUENCY |  | IfcTransformer.FREQUENCY
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Electrical design (partial requirements)
Symbol | X
Length |  |  | X | X | X
Width |  |  | X | X | X
Height |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_TransformerTypeCommon.Status |  | Pset_TransformerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Transformer power |  |  |  |  | X | X | Pset_TransformerTypeCommon.MaximumApparentPower |  | Pset_TransformerTypeCommon.MaximumApparentPower |  | Pset_TransformerTypeCommon.MaximumApparentPower
Electrical design (partial requirements)
Transformer power |  |  | X | X | X | X | Pset_TransformerTypeCommon.MaximumApparentPower |  | Pset_TransformerTypeCommon.MaximumApparentPower |  | Pset_TransformerTypeCommon.MaximumApparentPower
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5020.10 – Electrical Service and Distribution G4010.30 – Electrical Substations G4010.40 – Electrical Transformers G4050.10 – Area Lighting
DIN276 |  | KG 441 – Hoch- und Mittelspannungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electrical transformer

## Electricity storage
Electricity storage
Return to overview
General
An electricity storage device serves to store energy, in different forms: chemical, capacitive, inductive. It stores incoming electrical energy and releases it as and when needed. These devices also serve to "clean" an electric current by removing certain elements of the electric current generated by the electric power elements: capacitive phase shift, inductive phase shift, harmonics.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Battery (chemical storage) |  | IfcElectricFlowStorageDeviceType.BATTERY | [5 empty] | IfcElectricFlowStorageDevice.BATTERY |  | IfcElectricFlowStorageDevice.BATTERY
Capacitor bank |  | IfcElectricFlowStorageDeviceType.CAPACITORBANK | [5 empty] | IfcElectricFlowStorageDevice.CAPACITORBANK |  | IfcElectricFlowStorageDevice.CAPACITORBANK
Compensation battery |  | IfcElectricFlowStorageDeviceType.CAPACITORBANK | [5 empty] | IfcElectricFlowStorageDevice.CAPACITORBANK |  | IfcElectricFlowStorageDevice.CAPACITORBANK
Anti-harmonic |  | IfcElectricFlowStorageDeviceType.HARMONICFILTER | [5 empty] | IfcElectricFlowStorageDevice.HARMONICFILTER |  | IfcElectricFlowStorageDevice.HARMONICFILTER
Compensation inductor |  | IfcElectricFlowStorageDeviceType.INDUCTORBANK | [5 empty] | IfcElectricFlowStorageDevice.INDUCTORBANK |  | IfcElectricFlowStorageDevice.INDUCTORBANK
UPS/no-break |  | IfcElectricFlowStorageDeviceType.UPS | [5 empty] | IfcElectricFlowStorageDevice.UPS |  | IfcElectricFlowStorageDevice.UPS
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
Precasting (partial requirements)
Maintenance intervention volume |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_ElectricFlowStorageDeviceType.Status1 |  | Pset_ElectricFlowStorageDeviceTypeCommon.Status |  | Pset_ElectricFlowStorageDeviceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Nominal supply voltage |  |  |  |  | X | X | ePset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage1 |  | Pset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage |  | Pset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage
Electrical design (partial requirements)
Nominal supply voltage |  |  |  | X | X | X | ePset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage1 |  | Pset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage |  | Pset_ElectricFlowStorageDeviceTypeCommon.NominalSupplyVoltage
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5010.20 – Battery Equipment
DIN276 |  | KG 442 – Eigenstromversorgungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Electricity storage

## Extinguisher
Extinguisher
Return to overview
General
An extinguisher is a fire or heat-fighting device that can project or spread an appropriate substance (an "extinguishing agent") in order to put out the beginning of a fire. This extinguisher is generally portable but there are also mobile (wheeled) and fixed versions. (Source : Wikipedia)
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
﻿ |  | IfcFlowTerminal - [IfcFireSuppressionTerminalType] IfcFireSuppressionTerminalTypeEnum | [5 empty] | IfcFireSuppressionTerminal - IfcFireSuppressionTerminalTypeEnum
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4030.30 – Fire Extinguishers
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Extinguisher

## False ceiling
False ceiling
Return to overview
General
A suspended or false ceiling serves to conceal the technical and/or structural elements which pass above the ceiling. With a dismantlable ceiling, the ceiling tiles can be easily opened for adapting the technical equipment to the evolving needs of the premises.
A suspended ceiling generally consists of:
- adjustable hangers fixed to the structure
- (In certain cases) a metallic structure
- removable panels or a continuous finish (e.g. rendered plasterboard…)
Other data sheets for floors, slabs and ceilings : slab-on-grade, slab, technical floor.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
False ceiling |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | [5 empty] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
Suspended ceiling |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | [5 empty] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
Vertical ceiling closing |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | [5 empty] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
Technical ceiling |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING] | [5 empty] | IfcCovering.USERDEFINED[SUSPENDED_CEILING] |  | IfcCovering.USERDEFINED[SUSPENDED_CEILING]
Battens |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
When exporting a suspended ceiling, it is possible to export the assembly as a whole with its components (layers, profiles…), with the components as sub-entities of the global ceiling. It is also possible to decompose the ceiling on export, in which case each sub-component is an IFC element in its own right. The sub-components of a suspended ceiling are:
- Global suspended ceiling: IfcCovering – CEILING
- Ceiling panels: IfcCovering – CEILING (ceiling finishing)
- Sub-construction: IfcMember (linear structural element)
- Hangers: IfcColumn (column) or IfcMember (linear structural element)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Inspection trap door - dimensions |  |  |  | X | X
Reservations |  |  |  | X | X
Profile of structural elements - dimensions |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Maintenance (partial requirements)
Thickness |  |  |  |  | X | X
Thickness of each layer |  |  |  |  | X | X
Perimeter |  |  |  |  | X | X
Inspection trap door - dimensions |  |  |  |  | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions | X |  | X | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Access management (partial requirements)
Inspection trap door - dimensions |  |  |  | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Profile of structural elements - dimensions |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | ePset_CoveringCommon.IsExternal1 |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating
Thermal transmittance |  |  |  |  | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Acoustic resistance |  |  |  |  | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Flammability rating |  |  |  |  | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Thermal conductivity |  |  |  |  | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Heat loss calculation
Thermal conductivity |  |  | X | X |  |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B3080.10 – Exterior Ceiling C1070 – Suspended Ceiling Construction C2050 – Ceiling Finishing
DIN276 |  | KG 354 – Deckenbekleidungen KG 364 – Dachbekleidungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
False ceiling

## Fan
Fan
Return to overview
General
A fan is a mechanical element intended to set a gas, generally air, in motion, for blowing it into and/or extracting it from a building through the ventilation system. It can be centralised or decentralised. A fan can be a sub-component of a more diversified device: A.H.U. (air handling unit), double flow ventilation unit with heat recovery…
Other sheets for ventilation elements: air-to-air exchanger, filter, air handling unit (AHU), fan, ventilation duct, ventilation duct connection, vent.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fan |  | IfcFanType | [5 empty] | IfcFan |  | IfcFan
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowMovingDeviceTypeCommon.Status1 |  | Pset_FanTypeCommon.Status |  | Pset_FanTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Nominal flow |  |  |  |  | X | X | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
PEB (partial requirements)
Nominal flow |  |  | X | X | X | X | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate
Sanitary/HVAC design (partial requirements)
Nominal flow |  |  |  | X | X | X | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate |  | Pset_FanTypeCommon.NominalAirFlowRate
Electrical design (partial requirements)
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3050.50 – HVAC Air Distribution D3060 – Ventilation E1060.70 – Residential Ceiling Fans
DIN276 |  | KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Fan

## Filter
Filter
Return to overview
General
A ventilation filter serves to remove or at least reduce particulate matter or gases from the air.
Other data sheets for ventilation accessories: fan, air-to-air exchanger, air handling unit (AHU), ventilation air terminal, silencer, damper and register.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Air filter (G4, F7,etc.) |  | IfcFilterType.AIRPARTICLEFILTER | [5 empty] | IfcFilter.AIRPARTICLEFILTER |  | IfcFilter.AIRPARTICLEFILTER
HEPA filter |  | IfcFilterType.AIRPARTICLEFILTER | [5 empty] | IfcFilter.AIRPARTICLEFILTER |  | IfcFilter.AIRPARTICLEFILTER
Electrostatic filter |  | IfcFilterType.AIRPARTICLEFILTER | [5 empty] | IfcFilter.AIRPARTICLEFILTER |  | IfcFilter.AIRPARTICLEFILTER
Oil filter |  | IfcFilterType.OILFILTER | [5 empty] | IfcFilter.OILFILTER |  | IfcFilter.OILFILTER
Cyclone filter |  | IfcFilterType.WATERFILTER | [5 empty] | IfcFilter.WATERFILTER |  | IfcFilter.WATERFILTER
Water filter |  | IfcFilterType.WATERFILTER | [5 empty] | IfcFilter.WATERFILTER |  | IfcFilter.WATERFILTER
Active carbon filter (water and air) |  | IfcFilterType.ODORFILTER | [5 empty] | IfcFilter.ODORFILTER |  | IfcFilter.ODORFILTER
UV lamp (water treatment) |  | IfcFilterType.WATERFILTER | [5 empty] | IfcFilter.WATERFILTER |  | IfcFilter.WATERFILTER
UV lamp (air treatment) |  | IfcFilterType.AIRPARTICLEFILTER | [5 empty] | IfcFilter.AIRPARTICLEFILTER |  | IfcFilter.AIRPARTICLEFILTER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowTreamentDeviceTypeCommon.Status1 |  | Pset_FilterTypeCommon.Status |  | Pset_FilterTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3060.70 – HVAC Air Cleaning
DIN276 |  | KG421 – Wärmeerzeugungsalangen KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Filter

## Fire hose reel
Fire hose reel
Return to overview
General
A fire hose reel is a flexible hose that is connected to a hydrant in order to extinguish a fire. It is often supported by a reel and the ensemble is known as a hydrant or reel depending on the region
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fire hose reel |  | IfcFireSuppressionTerminalType.HOSEREEL | [5 empty] | IfcFireSuppressionTerminal.HOSEREEL |  | IfcFireSuppressionTerminal.HOSEREEL
Fire hose |  | IfcFireSuppressionTerminalType.HOSEREEL | [5 empty] | IfcFireSuppressionTerminal.HOSEREEL |  | IfcFireSuppressionTerminal.HOSEREEL
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Type of hose reel |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType
Mounting |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType
Diameter |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter
Length |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type of hose reel |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType
Mounting |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType
Diameter |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter
Length |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength
Fire safety (partial requirements)
Type of hose reel |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelType
Mounting |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseReelMountingType
Diameter |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseDiameter
Length |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength |  | Pset_FireSuppressionTerminalTypeHoseReel.HoseLength
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4010 – Fire Suppression
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Fire hose reel

## Fire hydrant
Fire hydrant
Return to overview
General
A fire hydrant serves to connect a fire hose to a water supply for extinguishing out a fire. Fire hydrants can be found inside buildings, generally in fire boxes (permanent supply = wet column, or solely as needed = dry column). Outdoors, there are fire hydrants connected to the city's water supply network.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fire hydrant |  | IfcFireSuppressionTerminalType.FIREHYDRANT | [5 empty] | IfcFireSuppressionTerminal.FIREHYDRANT |  | IfcFireSuppressionTerminal.FIREHYDRANT
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeFireHydrant.Status |  | Pset_FireSuppressionTerminalTypeFireHydrant.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type hydrant |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType |  | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType |  | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType
Number of connections |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections |  | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections |  | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections
Connection size |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize |  | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize |  | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize
Maximum pressure |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating |  | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating |  | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating
Fire safety (partial requirements)
Type hydrant |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType |  | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType |  | Pset_FireSuppressionTerminalTypeFireHydrant.FireHydrantType
Number of connections |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections |  | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections |  | Pset_FireSuppressionTerminalTypeFireHydrant.NumberOfHoseConnections
Connection size |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize |  | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize |  | Pset_FireSuppressionTerminalTypeFireHydrant.HoseConnectionSize
Maximum pressure |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating |  | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating |  | Pset_FireSuppressionTerminalTypeFireHydrant.PressureRating
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4010 – Fire Suppression
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Fire hydrant

## Fire protection cabinet
Fire protection cabinet
Return to overview
General
A fire cabinet is intended to centralise and store fire protection equipment in a way that is easily identifiable by its colour (red or white with red logo in Luxembourg and neighbouring countries). This cabinet can contain fire extinguishers, a fire hose or hose reel, a coupler for a distribution column and other accessories.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fire protection cabinet |  | IfcFireSuppressionTerminalType.USERDEFINED[FIRE_CABINETS] | [5 empty] | IfcFireSuppressionTerminal.USERDEFINED[FIRE_CABINETS] |  | IfcFireSuppressionTerminal.USERDEFINED[FIRE_CABINETS]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Status |  |  | X |  |  |  | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X |  |  |  | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4030.10 – Fire Protection Cabinets
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Fire protection cabinet

## Floor finishing
Floor finishing
Return to overview
General
This sheet contains all the finishing layers for interior and exterior floors. These are always non-load bearing layers.
Generally, the layers are modelled as multi-layers and the IFC export keeps these multi-layered walls, including the finishes. However, in some cases it is useful to have separate layers, and it is in these cases that the present GID sheet should be used :
- Spot finishing on a floor, e.g. parquet flooring on a partial area of a floor in a room in the middle of tiling, modelled with a single layer "slab" overlaying the general multi-layer slab.
- Need to have each layer separate in the IFC model (quantity extraction, work tracking by materials...). It is possible to break down the layers into individual objects when exporting IFC. Depending on the software you can specify an IFC class and type for each layer (PARTS Revit), the class is fixed in other software (Archicad, Allplan...).
- If the native modelling has been done layer by layer, then the mapping will have to be specified layer by layer, each layer being an independent IFC object.
Other related sheets : roof finishing, ceiling finishing, wall finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Raised tiling |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Linoleum |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Stone covering |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Wooden decking |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Wooden floor |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Parquet flooring |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Tiling |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Carpet |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Floor panel |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Mortar screed |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Dry screed |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Filling screed |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Levelling screed |  | IfcCovering.FLOORING | [5 empty] | IfcCovering.FLOORING |  | IfcCovering.FLOORING
Sandwich panel |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Battens |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Floor paint |  | IfcCovering.USERDEFINED[PAINTING] | [5 empty] | IfcCovering.USERDEFINED[FLOOR_PAINTING] |  | IfcCovering.USERDEFINED[PAINTING]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
Slope |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Slope |  |  |  | X | X
Peripheral profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Slope |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Handicap accessibility (partial requirements)
Slope |  |  | X | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
LCA (Life Cycle Analysis)
Status |  |  |  |  | X |  | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  |  |  | X |  | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Is external |  |  |  |  | X |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Thermal transmittance |  |  |  |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_WallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Layout plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Tables
Operating loads |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | C2030 – Flooring C2040 – Stair finishing
DIN276 |  | 324 – gründungsbeläge 353 – Deckenbeläge
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Floor finishing

## Foundation beam
Foundation beam
Return to overview
General
A foundation beam is used to distribute the loads of a structure over direct or deep foundations such as insulated footings, piles or foundation caissons.
Other sheets for direct and deep foundations : deep foundation, caisson foundation
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Foundation beam |  | IfcFooting.FOOTING_BEAM | [5 empty] | IfcFooting.FOOTING_BEAM |  | IfcFooting.FOOTING_BEAM
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
2D documents (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Global geometry |  |  | X |  | X
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Clash detection (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Reservations |  |  |  | X | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | ePset_FootingCommon.LoadBearing1 |  | Pset_FootingCommon.LoadBearing |  | Pset_FootingCommon.LoadBearing
Is load-bearing (Archicad) | X |  | X | X | X | X | ePset_FootingCommon.LoadBearing1 |  | Pset_FootingCommon.LoadBearing |  | Pset_FootingCommon.LoadBearing
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Geotechnical study report | X |  | X | X | X | X
Stability report |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A1020.80 – Grade Beams
DIN276 |  | 322 – Flachgründungen und Bodenplatten 323 – Tiefgründungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Foundation footing
Foundation footing
Return to overview
General
A strip (or continuous) footing is an infrastructure work, generally in reinforced concrete, which takes up the loads from a structural element of a construction and transmits and distributes these loads directly onto the ground (trench bottom or base level). In this case we speak here of a direct foundation. For example, we find examples of strip footing under a wall.
Other data sheets for direct foundations : slab-on-grade.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Pad footing |  | IfcFooting.PAD_FOOTING | [5 empty] | IfcFooting.PAD_FOOTING |  | IfcFooting.PAD_FOOTING
Extra thickness slab (pad) |  | IfcFooting.PAD_FOOTING | [5 empty] | IfcFooting.PAD_FOOTING |  | IfcFooting.PAD_FOOTING
Strip footing |  | IfcFooting.STRIP_FOOTING | [5 empty] | IfcFooting.STRIP_FOOTING |  | IfcFooting.STRIP_FOOTING
Wall footing |  | IfcFooting.STRIP_FOOTING | [5 empty] | IfcFooting.STRIP_FOOTING |  | IfcFooting.STRIP_FOOTING
Extra thickness slab (strip) |  | IfcFooting.STRIP_FOOTING | [5 empty] | IfcFooting.STRIP_FOOTING |  | IfcFooting.STRIP_FOOTING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
2D documents (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Global geometry |  |  | X |  | X
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Clash detection (partial requirements)
Global geometry | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Fire safety (partial requirements)
Accessories and specific elements |  |  |  | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | ePset_FootingCommon.Status1 |  | Pset_FootingCommon.Status |  | Pset_FootingCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | ePset_FootingCommon.LoadBearing1 |  | Pset_FootingCommon.LoadBearing |  | Pset_FootingCommon.LoadBearing
Is load-bearing (Archicad) | X |  | X | X | X | X | ePset_FootingCommon.LoadBearing1 |  | Pset_FootingCommon.LoadBearing |  | Pset_FootingCommon.LoadBearing
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal conductivity |  |  | X |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Geotechnical study report | X |  | X | X | X | X
Stability report |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A1010.10 – Wall FoundationA4040 - Pits and Bases
DIN276 |  | 322 – Flachgründungen und Bodenplatten
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Furniture
Furniture
Return to overview
General
A furniture includes all the components of a piece of furniture or equipment fixed or not to the building, such as chair, desk, table ... both for indoor and outdoor use. Note that technical equipment (electrical, telecommunications, sanitary ...) do not belong to this category of object.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Chair |  | IfcFurnishingElement | [5 empty] | IfcFurniture.CHAIR |  | IfcFurniture.CHAIR
Table |  | IfcFurnishingElement | [5 empty] | IfcFurniture.TABLE |  | IfcFurniture.TABLE
Desk |  | IfcFurnishingElement | [5 empty] | IfcFurniture.DESK |  | IfcFurniture.DESK
Cabinet |  | IfcFurnishingElement | [5 empty] | IfcFurniture.FILECABINET |  | IfcFurniture.FILECABINET
Kitchen furniture |  | IfcFurnishingElement | [5 empty] | IfcFurniture.USERDEFINED[KITCHENFURNITURE] |  | IfcFurniture.USERDEFINED[KITCHENFURNITURE]
Shelf |  | IfcFurnishingElement | [5 empty] | IfcFurniture.SHELF |  | IfcFurniture.SHELF
Sofa |  | IfcFurnishingElement | [5 empty] | IfcFurniture.SOFA |  | IfcFurniture.SOFA
Armchair |  | IfcFurnishingElement | [5 empty] | IfcFurniture.CHAIR |  | IfcFurniture.CHAIR
Bed |  | IfcFurnishingElement | [5 empty] | IfcFurniture.BED |  | IfcFurniture.BED
Planter |  | IfcFurnishingElement | [5 empty] | IfcFurniture.USERDEFINED[PLANTER] |  | IfcFurniture.USERDEFINED[PLANTER]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Architectural design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Acoustics (partial requirements)
Height |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Accessories and specific elements |  |  |  | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | Pset_FurnitureTypeCommon.Status |  | Pset_FurnitureTypeCommon.Status |  | Pset_FurnitureTypeCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_FurnitureTypeCommon.Status |  | Pset_FurnitureTypeCommon.Status |  | Pset_FurnitureTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage1 |  | BIMids_Common.WorkPackage1 |  | BIMids_Common.WorkPackage1
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate2 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate2 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition2 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Architectural design (partial requirements)
Description |  |  |  | X | X | X | Pset_FurnitureTypeCommon.Description |  | Pset_FurnitureTypeCommon.Description |  | Pset_FurnitureTypeCommon.Description
Is physically attached |  |  |  | X | X | X | ePset_FurnitureTypeCommon.IsBuiltIn2 |  | Pset_FurnitureTypeCommon.IsBuiltIn |  | Pset_FurnitureTypeCommon.IsBuiltIn
Cabinet with lock | [5 empty] | X | Pset_FurnitureTypeFileCabinet.WithLock |  | Pset_FurnitureTypeFileCabinet.WithLock |  | Pset_FurnitureTypeFileCabinet.WithLock
Intrusion and surveillance (partial requirements)
Is physically attached |  |  |  | X | X | X | ePset_FurnitureTypeCommon.IsBuiltIn2 |  | Pset_FurnitureTypeCommon.IsBuiltIn |  | Pset_FurnitureTypeCommon.IsBuiltIn
Cabinet with lock |  |  |  | X | X | X | Pset_FurnitureTypeFileCabinet.WithLock |  | Pset_FurnitureTypeFileCabinet.WithLock |  | Pset_FurnitureTypeFileCabinet.WithLock
1) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
2) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | E2010 – Fixed Furnishings E2050 – Movable Furnishings
DIN276 |  | 381 – Allgemeinen Einbauten 473 – Medienversorgungsanlagen, Medizin- und labortechnische Anlagen 610 – Allgemeine Ausstattung
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Heat diffusion - radiator
Heat diffusion - radiator
Return to overview
General
Radiators use a combination of radiation and/or natural convection with a heat source such as electricity, steam or hot water to heat a space or a limited area. Radiators and heated towel rails are examples of heat diffusers with centralised generation. Electric radiators and towel-rails are examples of decentralised surface diffusion heating devices.
Other related data sheets: heat/cold diffusion - convector, heat/cold diffusion - surface.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Finned radiator |  | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | [5 empty] | IfcSpaceHeater.RADIATOR |  | IfcSpaceHeater.RADIATOR
Electric radiator |  | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | [5 empty] | IfcSpaceHeater.RADIATOR |  | IfcSpaceHeater.RADIATOR
Plate radiator |  | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | [5 empty] | IfcSpaceHeater.RADIATOR |  | IfcSpaceHeater.RADIATOR
Towel dryer |  | IfcSpaceHeaterType.USERDEFINED[RADIATOR] | [5 empty] | IfcSpaceHeater.RADIATOR |  | IfcSpaceHeater.RADIATOR
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_SpaceHeaterTypeCommon.Status |  | Pset_SpaceHeaterTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Radiator type |  |  |  |  | X | X | ePset_EnergyConversionDevice.RadiatorType1 |  | Pset_SpaceHeaterTypeRadiator.RadiatorType |  | Pset_SpaceHeaterTypeRadiator.RadiatorType
Type of placement |  |  |  |  | X | X | ePset_EnergyConversionDevice.PlacementType1 |  | Pset_SpaceHeaterTypeCommon.PlacementType |  | Pset_SpaceHeaterTypeCommon.PlacementType
PEB (partial requirements)
Radiator type |  |  | X | X | X | X | ePset_EnergyConversionDevice.RadiatorType1 |  | Pset_SpaceHeaterTypeRadiator.RadiatorType |  | Pset_SpaceHeaterTypeRadiator.RadiatorType
Sanitary/HVAC design (partial requirements)
Radiator type |  |  |  | X | X | X | ePset_EnergyConversionDevice.RadiatorType1 |  | Pset_SpaceHeaterTypeRadiator.RadiatorType |  | Pset_SpaceHeaterTypeRadiator.RadiatorType
Type of placement |  |  |  | X | X | X | ePset_EnergyConversionDevice.PlacementType1 |  | Pset_SpaceHeaterTypeCommon.PlacementType |  | Pset_SpaceHeaterTypeCommon.PlacementType
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3020.70 – Decentralized Heating Equipment
DIN276 |  | KG 423 – RaumHeizflächen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Heat diffusion - radiator

## Heat production - steam
Heat production - steam
Return to overview
General
A heating steam generation system is a closed tank in which water or another fluid is heated to a temperature above 100°C using an energy source such as natural gas, fuel oil or electricity. The fluid in the tank is then discharged from the device for use in various processes or heating applications.
The tank in question is used only for heating water or other fluids. Storage tanks, for example for storing drinking or rain water, are considered as reservoirs, access via the "reservoir" link below.
Other related data sheets: heat production - water, chiller, tank, air handling unit, radiator, heat/cold diffusion - convector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Boiler |  | IfcBoilerType.STEAM | [5 empty] | IfcBoiler.STEAM |  | IfcBoiler.STEAM
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_BoilerTypeCommon.Status |  | Pset_BoilerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Power source |  |  |  |  | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (steam) |  |  |  |  | X | X | Pset_BoilerTypeCommon.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency
Nominal heat output (steam) |  |  |  |  | X | X | Pset_BoilerTypeCommon.NominalEnergyConsumption |  | Pset_BoilerTypeCommon.NominalEnergyConsumption |  | Pset_BoilerTypeCommon.NominalEnergyConsumption
Effective load |  |  |  |  | X | X | ePset_BoilerPHistory.Load1 |  | Pset_BoilerPHistory.Load |  | Pset_BoilerPHistory.Load
Energy consumption |  |  |  |  | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency |  |  |  |  | X | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
PEB (partial requirements)
Power source |  |  | X | X | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (steam) |  |  | X | X | X | X | Pset_BoilerTypeCommon.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency
Energy consumption |  |  | X | X | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency | [5 empty] | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
Sanitary/HVAC design (partial requirements)
Power source |  |  | X | X | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (steam) |  |  | X | X | X | X | Pset_BoilerTypeCommon.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency |  | Pset_BoilerTypeSteam.NominalEfficiency
Effective load |  |  |  | X | X | X | ePset_BoilerPHistory.Load1 |  | Pset_BoilerPHistory.Load |  | Pset_BoilerPHistory.Load
Energy consumption |  |  | X | X | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency | [5 empty] | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D2010.20 – Domestic Water Heaters D3020.10 – Heat Generation
DIN276 |  | KG 412 – Wasseranlagen KG 421 – Wärmeerzeugungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Heat production - steam

## Heat production - water
Heat production - water
Return to overview
General
A water or fluid heating system consists of a closed, pressure-resistant tank in which water or another fluid is heated using an energy source such as natural gas, fuel oil or electricity. The fluid in the tank is then discharged from the device for use in various processes or heating applications.
The tank in question is used only for heating water or other fluids. Storage tanks, for example for storing drinking or rain water, are considered as reservoirs, access via the "reservoir" link below.
Other related data sheets: heat production - steam, tank, chiller, air handling unit, radiator, heat/cold diffusion - surface, heat/cold diffusion - convector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Thermodynamic balloon |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Water heater |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Hot water tank |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Oil boiler |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Gas boiler |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Air-water heat pump (including reversible) |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Ground-water heat pump (including reversible) |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Wood boiler |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
Pellet boiler |  | IfcBoilerType.WATER | [5 empty] | IfcBoiler.WATER |  | IfcBoiler.WATER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Sanitary/HVAC design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_BoilerTypeCommon.Status |  | Pset_BoilerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Power source |  |  |  |  | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (water) |  |  |  |  | X | X | ePset_BoilerTypeCommon.NominalEfficiency1 |  | Pset_BoilerTypeWater.NominalEfficiency |  | Pset_BoilerTypeWater.NominalEfficiency
Nominal heat output (water) |  |  |  |  | X | X | ePset_BoilerTypeCommon.NominalEnergyConsumption1 |  | Pset_BoilerTypeCommon.NominalEnergyConsumption |  | Pset_BoilerTypeCommon.NominalEnergyConsumption
Effective load |  |  |  |  | X | X | ePset_BoilerPHistory.Load1 |  | Pset_BoilerPHistory.Load |  | Pset_BoilerPHistory.Load
Energy consumption |  |  |  |  | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency |  |  |  |  | X | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
PEB (partial requirements)
Power source |  |  | X | X | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (water) |  |  | X | X | X | X | ePset_BoilerTypeCommon.NominalEfficiency1 |  | Pset_BoilerTypeWater.NominalEfficiency |  | Pset_BoilerTypeWater.NominalEfficiency
Nominal heat output (water) |  |  | X | X | X | X | ePset_BoilerTypeCommon.NominalEnergyConsumption1 |  | Pset_BoilerTypeCommon.NominalEnergyConsumption |  | Pset_BoilerTypeCommon.NominalEnergyConsumption
Energy consumption |  |  | X | X | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency | [5 empty] | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
Sanitary/HVAC design (partial requirements)
Power source |  |  | X | X | X | X | ePset_BoilerTypeCommon.EnergySource1 |  | Pset_BoilerTypeCommon.EnergySource |  | Pset_BoilerTypeCommon.EnergySource
Nominal efficiency (water) |  |  | X | X | X | X | ePset_BoilerTypeCommon.NominalEfficiency1 |  | Pset_BoilerTypeWater.NominalEfficiency |  | Pset_BoilerTypeWater.NominalEfficiency
Effective load |  |  |  | X | X | X | ePset_BoilerPHistory.Load1 |  | Pset_BoilerPHistory.Load |  | Pset_BoilerPHistory.Load
Energy consumption |  |  | X | X | X | X | ePset_BoilerPHistory.EnergySourceConsumption1 |  | Pset_BoilerPHistory.EnergySourceConsumption |  | Pset_BoilerPHistory.EnergySourceConsumption
Operational efficiency | [5 empty] | X | ePset_BoilerPHistory.OperationalEfficiency1 |  | Pset_BoilerPHistory.OperationalEfficiency |  | Pset_BoilerPHistory.OperationalEfficiency
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D2010.20 – Domestic Water Heaters D3020.10 – Heat Generation
DIN276 |  | KG 412 – Wasseranlagen KG 421 – Wärmeerzeugungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Heat production - water

## Heatcold diffusion - surface
Heat/cold diffusion - surface
Return to overview
General
Surface heat or cooling diffusers work by radiation via an exchanger (pipes, possibly with conductive diffusers) using a heat source such as electricity, steam or hot water to heat a space or a limited area. Wet underfloor heating (water pipes in screed) and dry underfloor heating (pipes clipped into profile + metal mesh diffuser under the floor covering), underfloor heating with direct expansion of the refrigerant gas, and active false ceilings are all examples of surface heat diffusers with centralised generation. Electrically heated floors and ceilings are examples of local surface diffusion heating devices.
Other related data sheets : heat diffusion - radiator, heat/cooling diffusion - convector
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Radiant floor heating |  | IfcCoilType.WATERHEATINGCOIL | [5 empty] | IfcCoil.WATERHEATINGCOIL |  | IfcCoil.WATERHEATINGCOIL
Radiant floor cooling |  | IfcCoilType.WATERCOOLINGCOIL | [5 empty] | IfcCoil.WATERCOOLINGCOIL |  | IfcCoil.WATERCOOLINGCOIL
Radiant floor heating/cooling |  | IfcCoilType.HYDRONICCOIL | [5 empty] | IfcCoil.HYDRONICCOIL |  | IfcCoil.HYDRONICCOIL
Direct expansion floor heating |  | IfcCoilType.DXCOOLINGCOIL | [5 empty] | IfcCoil.DXCOOLINGCOIL |  | IfcCoil.DXCOOLINGCOIL
Active heating ceiling (water) |  | IfcCoilType.WATERHEATINGCOIL | [5 empty] | IfcCoil.WATERHEATINGCOIL |  | IfcCoil.WATERHEATINGCOIL
Active cooling ceiling (water) |  | IfcCoilType.WATERCOOLINGCOIL | [5 empty] | IfcCoil.WATERCOOLINGCOIL |  | IfcCoil.WATERCOOLINGCOIL
Active cooling/heating ceiling (water) |  | IfcCoilType.HYDRONICCOIL | [5 empty] | IfcCoil.HYDRONICCOIL |  | IfcCoil.HYDRONICCOIL
Electric radiant ceiling |  | IfcCoilType.ELECTRICHEATINGCOIL | [5 empty] | IfcCoil.ELECTRICHEATINGCOIL |  | IfcCoil.ELECTRICHEATINGCOIL
Electric radiant floor |  | IfcCoilType.ELECTRICHEATINGCOIL | [5 empty] | IfcCoil.ELECTRICHEATINGCOIL |  | IfcCoil.ELECTRICHEATINGCOIL
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_CoilTypeCommon.Status |  | Pset_CoilTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type of placement |  |  |  |  | X | X | ePset_CoilTypeCommon.PlacementType1 |  | Pset_CoilTypeCommon.PlacementType |  | Pset_CoilTypeCommon.PlacementType
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3020.70 – Decentralized Heating Equipment D3030.70 Decentralized Cooling
DIN276 |  | KG 423 – RaumHeizflächen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Heat/cold diffusion - surface

## Heatcold distribution - convect
Heat/cold distribution - convector
Return to overview
General
Convectors use a combination of radiation and/or convection (natural or forced) with a heat source such as electricity, steam or hot water to heat a space or a limited area. Convectors, skirting boards and finned tubes are examples of supplementary heating devices (space heaters).
Other related data sheets: heat diffusion - radiator, heat/cold diffusion - surface.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Baseboard heaters |  | IfcSpaceHeaterType.CONVECTOR | [5 empty] | IfcSpaceHeater.CONVECTOR |  | IfcSpaceHeater.CONVECTOR
Finned tubes |  | IfcSpaceHeaterType.CONVECTOR | [5 empty] | IfcSpaceHeater.CONVECTOR |  | IfcSpaceHeater.CONVECTOR
Fan coil unit |  | IfcSpaceHeaterType.CONVECTOR | [5 empty] | IfcSpaceHeater.CONVECTOR |  | IfcSpaceHeater.CONVECTOR
IfcUnitaryEquipment should be used for enclosed units supporting a combination of heating, cooling and/or dehumidification
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_SpaceHeaterTypeCommon.Status |  | Pset_SpaceHeaterTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Convector type |  |  |  |  | X | X | ePset_EnergyConversionDevice.ConvectorType1 |  | Pset_SpaceHeaterTypeConvector.ConvectorType |  | Pset_SpaceHeaterTypeConvector.ConvectorType
Type of placement |  |  |  |  | X | X | ePset_EnergyConversionDevice.PlacementType1 |  | Pset_SpaceHeaterTypeCommon.PlacementType |  | Pset_SpaceHeaterTypeCommon.PlacementType
PEB (partial requirements)
Convector type |  |  | X | X | X | X | ePset_EnergyConversionDevice.ConvectorType1 |  | Pset_SpaceHeaterTypeConvector.ConvectorType |  | Pset_SpaceHeaterTypeConvector.ConvectorType
Sanitary/HVAC design (partial requirements)
Convector type |  |  | X | X | X | X | ePset_EnergyConversionDevice.ConvectorType1 |  | Pset_SpaceHeaterTypeConvector.ConvectorType |  | Pset_SpaceHeaterTypeConvector.ConvectorType
Type of placement |  |  |  | X | X | X | ePset_EnergyConversionDevice.PlacementType1 |  | Pset_SpaceHeaterTypeCommon.PlacementType |  | Pset_SpaceHeaterTypeCommon.PlacementType
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3020.70 – Decentralized Heating Equipment D3030.70 Decentralized Cooling
DIN276 |  | KG 423 – RaumHeizflächen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Heat/cold diffusion - convector

## Lift
Lift
Return to overview
General
A lift is an item of transport equipment that serves to transport persons and/or goods between two different levels of a building in a closed cabin or car.
Other data sheet for transport equipment : transport equipment (excluding lift).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Lift |  | IfcTransportElement.ELEVATOR | [5 empty] | IfcTransportElement.ELEVATOR |  | IfcTransportElement.ELEVATOR
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
Fire safety (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Handicap accessibility (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Technical rooms - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_TransportElementCommon.Status1 |  | Pset_TransportElementCommon.Status |  | Pset_TransportElementCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_TransportElementCommon.Status |  | Pset_TransportElementCommon.Status |  | Pset_TransportElementCommon.Status
Is external | X |  | X | X | X | X | Pset_TransportElementCommon.IsExternal |  | Pset_TransportElementCommon.IsExternal |  | Pset_TransportElementCommon.IsExternal
Is external (Archicad) | X |  | X | X | X | X | Pset_TransportElementCommon.IsExternal |  | Pset_TransportElementCommon.IsExternal |  | Pset_TransportElementCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Is firemen access |  |  |  |  | X | X | ePset_TransportElementElevator.FireFightingLift1 |  | Pset_TransportElementElevator.FireFightingLift |  | Pset_TransportElementElevator.FireFightingLift
Cabin width |  |  |  |  | X | X | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth
Cabin depth |  |  |  |  | X | X | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth
Cabin height |  |  |  |  | X | X | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight
Capacity in weight |  |  |  |  | X | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  |  |  | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Access management (partial requirements)
Is firemen access |  |  |  | X | X | X | ePset_TransportElementElevator.FireFightingLift1 |  | Pset_TransportElementElevator.FireFightingLift |  | Pset_TransportElementElevator.FireFightingLift
Cabin width |  |  |  | X | X | X | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth
Cabin depth |  |  |  | X | X | X | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth
Cabin height |  |  |  | X | X | X | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight
Capacity in weight |  |  |  | X | X | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  |  | X | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Fire safety (partial requirements)
Is firemen access |  |  | X | X | X | X | ePset_TransportElementElevator.FireFightingLift1 |  | Pset_TransportElementElevator.FireFightingLift |  | Pset_TransportElementElevator.FireFightingLift
Cabin width |  |  | X | X | X | X | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth
Cabin depth |  |  | X | X | X | X | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth
Cabin height |  |  | X | X | X | X | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight
Capacity in weight | [5 empty] | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons | [5 empty] | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Building permit (partial requirements)
Cabin width |  |  | X |  |  |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth
Cabin depth |  |  | X |  |  |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth
Cabin height |  |  | X |  |  |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight
Capacity in weight |  |  | X |  |  |  | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  | X |  |  |  | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Handicap accessibility (partial requirements)
Cabin width |  |  | X | X | X | X | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth |  | Pset_TransportElementElevator.ClearWidth
Cabin depth |  |  | X | X | X | X | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth |  | Pset_TransportElementElevator.ClearDepth
Cabin height |  |  | X | X | X | X | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight |  | Pset_TransportElementElevator.ClearHeight
Capacity in persons |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Electrical design (partial requirements)
Capacity in weight |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D1010.10 – Elevators
DIN276 |  | KG461 – Aufzugsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Lightfixture
Lightfixture
Return to overview
General
A light fixture is intended to provide artificial lighting, it can include the light fixture itself but also the lamp(s), transformer, dimmers and other accessories.
Other data sheet relating to lighting: safety lighting.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Beam lighting |  | IfcLightFixtureType.POINTSOURCE | [5 empty] | IfcLightFixture.POINTSOURCE |  | IfcLightFixture.POINTSOURCE
Multidirectional lighting |  | IfcLightFixtureType.DIRECTIONSOURCE | [5 empty] | IfcLightFixture.DIRECTIONSOURCE |  | IfcLightFixture.DIRECTIONSOURCE
The components of an IfcLightFixture are:
- Lamp: IfcFlowTerminal (IFC2x3) and IfcLamp (IFC4)- COMPACTFLUORESCENT - FLUORESCENT - HIGHPRESSUREMERCURY - HIGHTPRESSURESODIUM - METALHALIDE - TUNGSTENFILAMENT - USERDEFINED - NOTDEFINED, IFC4 seulement : HALOGEN - LED - OLED
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Fire safety (partial requirements)
Symbol |  |  |  | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Electrical design (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X
Width |  |  |  |  | X
Height |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FlowTerminalTypeCommon.Status1 |  | Pset_LightFixtureTypeCommon.Status |  | Pset_LightFixtureTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_LightFixtureTypeCommon.Status1 |  | Pset_LightFixtureTypeCommon.Status |  | Pset_LightFixtureTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Maintenance factor |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.MaintenanceFactor |  | Pset_LightFixtureTypeCommon.MaintenanceFactor |  | Pset_LightFixtureTypeCommon.MaintenanceFactor
Luminous flux |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Placement |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType
Electrical power |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Type of mounting |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
Fire safety (partial requirements)
Luminous flux3 |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Handicap accessibility (partial requirements)
Luminous flux3 |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Intrusion and surveillance (partial requirements)
Luminous flux3 |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Placement |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType
Electrical power |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Electrical design (partial requirements)
Electrical power |  |  |  | X | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Type of mounting |  |  |  | X | X | X | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
3) Relates to another IFC class (IfcLamp)
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5040.50 – Lighting Fixtures
DIN276 |  | KG445 – Beleuchtungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Lightfixture

## Linear structural member
Linear structural member
Return to overview
General
A frame element is a horizontal, vertical or oblique linear construction element (posts and columns excluded), generally in wood/steel/concrete, serving to transfer loads by bending and/or compression and/or traction. The structural elements can be components of the roof structure (purlin, rafters, component of a truss), the floor structure but also components of lattice beams (lower and upper cross-members, vertical and oblique uprights), bracings for buildings, wall structure elements (timber frame, curtain wall, etc.), etc.
Other data sheets for linear structural member : foundation beam, beam, column.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Floor joist |  | IfcMember.USERDEFINED[JOIST] | [5 empty] | IfcMember.USERDEFINED[JOIST] |  | IfcMember.USERDEFINED[JOIST]
Vertical timber frame element |  | IfcMember.STUD | [5 empty] | IfcMember.STUD |  | IfcMember.STUD
Horizontal beam timber frame |  | IfcMember.PLATE | [5 empty] | IfcMember.PLATE |  | IfcMember.PLATE
Rafter |  | IfcMember.RAFTER | [5 empty] | IfcMember.RAFTER |  | IfcMember.RAFTER
Bracing |  | IfcMember.BRACE | [5 empty] | IfcMember.BRACE |  | IfcMember.BRACE
Stringer |  | IfcMember.STRINGER | [5 empty] | IfcMember.STRINGER |  | IfcMember.STRINGER
Mullion |  | IfcMember.MULLION | [5 empty] | IfcMember.MULLION |  | IfcMember.MULLION
Curtain wall mullion |  | IfcMember.MULLION | [5 empty] | IfcMember.MULLION |  | IfcMember.MULLION
Purlin |  | IfcMember.PURLIN | [5 empty] | IfcMember.PURLIN |  | IfcMember.PURLIN
Chord |  | IfcMember.CHORD | [5 empty] | IfcMember.CHORD |  | IfcMember.CHORD
Wall plate |  | IfcMember.PURLIN | [5 empty] | IfcMember.PURLIN |  | IfcMember.PURLIN
Battens |  | IfcMember.RAFTER | [5 empty] | IfcMember.RAFTER |  | IfcMember.RAFTER
Hip rafter |  | IfcMember.RAFTER | [5 empty] | IfcMember.RAFTER |  | IfcMember.RAFTER
Ridge beam |  | IfcMember.PURLIN | [5 empty] | IfcMember.PURLIN |  | IfcMember.PURLIN
Top chord |  | IfcMember.CHORD | [5 empty] | IfcMember.CHORD |  | IfcMember.CHORD
Collar tie |  | IfcMember.COLLAR | [5 empty] | IfcMember.COLLAR |  | IfcMember.COLLAR
King post |  | IfcMember.POST | [5 empty] | IfcMember.POST |  | IfcMember.POST
Strut |  | IfcMember.STRUT | [5 empty] | IfcMember.STRUT |  | IfcMember.STRUT
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Precasting (partial requirements)
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Slope |  |  |  | X | X
Section profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Fire safety (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Architectural design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Slope |  |  | X |  | X
Section profile |  |  |  |  | X
Acoustics (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Section profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Section profile |  |  |  | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_MemberCommon.Status1 |  | Pset_MemberCommon.Status |  | Pset_MemberCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | Pset_MemberCommon.Status |  | Pset_MemberCommon.Status |  | Pset_MemberCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) |  |  | X | X | X | X | Pset_MemberCommon.LoadBearing |  | Pset_MemberCommon.LoadBearing |  | Pset_MemberCommon.LoadBearing
Is load-bearing (Archicad) |  |  | X | X | X | X | ePset_RoofCommon.LoadBearing1 |  | Pset_MemberCommon.LoadBearing |  | Pset_MemberCommon.LoadBearing
Is external |  |  | X | X | X | X | Pset_MemberCommon.IsExternal |  | Pset_MemberCommon.IsExternal |  | Pset_MemberCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | Pset_MemberCommon.ThermalTransmittance |  | Pset_MemberCommon.ThermalTransmittance |  | Pset_MemberCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  |  | X | X | X | Pset_MemberCommon.FireRating |  | Pset_MemberCommon.FireRating |  | Pset_MemberCommon.FireRating
Flammability rating |  |  |  | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Acoustics (partial requirements)
Is outer shell |  |  |  | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1010.10 – Floor Structural Frame B1020.10 – Roof Structural Frame B2010.20 – Exterior Wall Construction B3080.10 – Exterior Ceiling C1010 – Interior Partition F1020.40 – Metal Building Systems
DIN276 |  | 331 – Tragende Außenwände 351 – Deckenkonstruktionen 355 – Elementierte Deckenkonstruktionen 361 – Dachkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Management panel
Management panel
Return to overview
General
A controller is a device that monitors inputs and controls outputs in a building automation system.
A controller can be physical (placed in a spatial structure) or logical (a software interface or aggregated in a programmable physical controller).
Other data sheets GTB : actuator
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Management panel |  | IfcDistributionControlElement | [5 empty] | IfcUnitaryControlElement.CONTROLPANEL |  | IfcUnitaryControlElement.CONTROLPANEL
Fire alarm control panel |  | IfcDistributionControlElement | [5 empty] | IfcUnitaryControlElement.ALARMPANEL |  | IfcUnitaryControlElement.ALARMPANEL
Alarm control panel |  | IfcDistributionControlElement | [5 empty] | IfcUnitaryControlElement.ALARMPANEL |  | IfcUnitaryControlElement.ALARMPANEL
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Electrical design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X
Width |  |  |  | X | X
Height |  |  |  | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_DistributionControlElementTypeCommon.Status1 |  | Pset_ControllerTypeCommon.Status |  | Pset_ControllerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D8010.10 – Integrated Automation Control of Equipment D8010.20 – Integrated Automation Control of Conveying Equipment D8010.30 – Integrated Automation Control of Fire-Suppression Systems D8010.40 – Integrated Automation Control of Plumbing Systems D8010.50 – Integrated Automation Control of HVAC Systems D8010.60 – Integrated Automation Control of Electrical Systems D8010.70 – Integrated Automation Control of Communication Systems D8010.80 – Integrated Automation Control of Electronic Safety and Security Systems D8010.90 – Integrated Automation Supplementary Components
DIN276 |  | KG 481 – Automationseinrichtungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Management panel

## Pump
Pump
Return to overview
General
A pump is a device that transmits mechanical force to fluids or sludge in order to move them through a pipeline. A pump can be part of various networks, such as the water supply network (hot water loop, booster), the heating/cooling network (circulator for heat/cooling distribution, oil pump, pump), the sewer system (lift pump), and the fire extinguishing network.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Generic pump |  | IfcPumpType.USERDEFINED[GENERIC] | [5 empty] | IfcPump.USERDEFINED[GENERIC] |  | IfcPump.USERDEFINED[GENERIC]
Circulator |  | IfcPumpType.CIRCULATOR | [5 empty] | IfcPump.CIRCULATOR |  | IfcPump.CIRCULATOR
Oil pump |  | IfcPumpType.USERDEFINED[OILPUMP] | [5 empty] | IfcPump.USERDEFINED[OILPUMP] |  | IfcPump.USERDEFINED[OILPUMP]
Lift pump |  | IfcPumpType.USERDEFINED[SUMP_PITS] | [5 empty] | IfcPump.USERDEFINED[SUMP_PITS] |  | IfcPump.USERDEFINED[SUMP_PITS]
Booster pump |  | IfcPumpType.USERDEFINED[WATERBOOSTER] | [5 empty] | IfcPump.USERDEFINED[WATERBOOSTER] |  | IfcPump.USERDEFINED[WATERBOOSTER]
Water pump |  | IfcPumpType.USERDEFINED[WATERSUPPLY] | [5 empty] | IfcPump.USERDEFINED[WATERSUPPLY] |  | IfcPump.USERDEFINED[WATERSUPPLY]
Fire pump |  | IfcPumpType.USERDEFINED[FIREPROTECTION] | [5 empty] | IfcPump.USERDEFINED[FIREPROTECTION] |  | IfcPump.USERDEFINED[FIREPROTECTION]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FlowMovingDeviceTypeCommon.Status1 |  | Pset_PumpTypeCommon.Status |  | Pset_PumpTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Flow rate range |  |  |  |  | X | X | Pset_PumpTypeCommon.FlowRateRange |  | Pset_PumpTypeCommon.FlowRateRange |  | Pset_PumpTypeCommon.FlowRateRange
Connection size |  |  |  |  | X | X | Pset_PumpTypeCommon.ConnectionSize |  | Pset_PumpTypeCommon.ConnectionSize |  | Pset_PumpTypeCommon.ConnectionSize
Sanitary/HVAC design (partial requirements)
Flow rate range |  |  |  | X | X | X | Pset_PumpTypeCommon.FlowRateRange |  | Pset_PumpTypeCommon.FlowRateRange |  | Pset_PumpTypeCommon.FlowRateRange
Connection size |  |  |  | X | X | X | Pset_PumpTypeCommon.ConnectionSize |  | Pset_PumpTypeCommon.ConnectionSize |  | Pset_PumpTypeCommon.ConnectionSize
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D2010.20 Domestic Water Equipement D2010.40 – Domestic Water Piping D2020.10 – Sanitary Sewerage Equipement D2030.10 – Stormwater Drainage Equipement D3010.30 – Fuel Pump D3020.10 – Heat Generation (Boiler feedwater Pumps) D3050.10 Facility Hydronic Distribution D3050.30 Facility Steam Distribution D4010.10 Fire Suppression F1050.10 – Pools F1050.20 – Interior Fountains G2060.10 – Exterior Foutains G2080.10 – Planting Irrigation G3010.10 Site Domestic Water Distribution G3010.30 Site Fire Protection Water Distribution G3010.50 – Site Irrigation Water Distribution G3020.40 Utility Septic Tank G3030.50 – Storm Drainage Pumps G3050.10 – Site Hydronic Heating Distribution G3050.40 – Site Hydronic Cooling Distribution G3060 – Site Fuel Distribution
DIN276 |  | KG 412 – Wasseranlagen KG 421 – Wärmeerzeugunganlagen KG 422 – Wärmeverteilnetze
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Pump

## Ramp
Ramp
Return to overview
General
A ramp is an inclined surface construction element that connects spaces at different levels on foot or with a wheeled vehicle (wheelchair, car, etc.). It does not normally have a step. A ramp may consist of one or more inclined planes separated by horizontal landings. There is a difference between a ramp laid on the ground and a ramp that is supported:
A ramp on the ground is laid on the ground by means of sub-layers (insulation, waterproofing, draining stonework, etc.) and is not intended to transmit the loads of the building (except for its own load and the loads of use on the ramp transmitted directly to the ground). A load-bearing ramp divides the spaces of a building horizontally (like a slab). This element is composed of a load-bearing structural part which transfers the loads to vertical load-bearing elements (walls, columns), possibly via beams.
Other related sheets : slab, slab-on-grade, roof, stairs, roof finishing, ceiling finishing, floor finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Straight run ramp |  | IfcRamp.STRAIGHT_RUN_RAMP | [5 empty] | IfcRamp.STRAIGHT_RUN_RAMP |  | IfcRamp.STRAIGHT_RUN_RAMP
Two straight run ramp |  | IfcRamp.TWO_STRAIGHT_RUN_RAMP | [5 empty] | IfcRamp.TWO_STRAIGHT_RUN_RAMP |  | IfcRamp.TWO_STRAIGHT_RUN_RAMP
Quarter turn ramp |  | IfcRamp.QUARTER_TURN_RAMP | [5 empty] | IfcRamp.QUARTER_TURN_RAMP |  | IfcRamp.QUARTER_TURN_RAMP
Two quarter turn ramp |  | IfcRamp.TWO_QUARTER_TURN_RAMP | [5 empty] | IfcRamp.TWO_QUARTER_TURN_RAMP |  | IfcRamp.TWO_QUARTER_TURN_RAMP
Half turn ramp |  | IfcRamp.HALF_TURN_RAMP | [5 empty] | IfcRamp.HALF_TURN_RAMP |  | IfcRamp.HALF_TURN_RAMP
Spiral ramp |  | IfcRamp.SPIRAL_RAMP | [5 empty] | IfcRamp.SPIRAL_RAMP |  | IfcRamp.SPIRAL_RAMP
Sloping ramp |  | IfcRamp.STRAIGHT_RUN_RAMP | [5 empty] | IfcRamp.STRAIGHT_RUN_RAMP |  | IfcRamp.STRAIGHT_RUN_RAMP
The components of an IfcRamp are:
- Inclined plane: IfcRampFlight (IFC2x3 and IFC4) – STRAIGHT – SPIRAL – USERDEFINED – NOTDEFINED
- Landing: IfcSlab – LANDING (see Slab)
- Railing: IfcRailing (IFC2x3 and IFC4) – HANDRAIL – GARDRAIL – BALUSTRADE – USERDEFINED – NOTDEFINED (A separate data sheet will be published later)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Slope | X |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Slope |  |  | X
Flight - dimensions |  |  | X
Landing - dimensions |  |  | X
Railing - dimensions |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Flight - dimensions |  |  | X | X | X | X
Landing - dimensions |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Slope |  |  |  | X | X
Flight - dimensions |  |  |  | X | X
Landing - dimensions |  |  |  | X | X
Railing - dimensions |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Slope | X |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Slope | X |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Slope |  |  |  |  | X
Flight - dimensions |  |  |  |  | X
Landing - dimensions |  |  |  |  | X
Railing - dimensions |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Flight - dimensions |  |  | X | X | X | X
Landing - dimensions |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Slope | X |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Handicap accessibility (partial requirements)
Slope | X |  | X | X | X | X
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Fire safety (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcElementAttributes.ShapeType |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_RampCommon.Status1 |  | Pset_RampCommon.Status |  | Pset_RampCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_RampCommon.Status |  | Pset_RampCommon.Status |  | Pset_RampCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | Pset_RampCommon.LoadBearing |  | Pset_RampCommon.LoadBearing |  | Pset_RampCommon.LoadBearing
Is load-bearing (Archicad) | X |  | X | X | X | X | Pset_RampCommon.LoadBearing |  | Pset_RampCommon.LoadBearing |  | Pset_RampCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_RampCommon.IsExternal |  | Pset_RampCommon.IsExternal |  | Pset_RampCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  |  |  | X |  | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_RampCommon.FireRating |  | Pset_RampCommon.FireRating |  | Pset_RampCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance |  | Pset_RampCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Specifications | X |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1010.50 – Ramps
DIN276 |  | 351 – Deckenkonstruktionen 355 – Elementierte Deckenkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Ramp

## Roof
Roof
Return to overview
General
A roof is a surface element, flat or otherwise, horizontal or inclined, which closes off the upper part of the spaces of a building against the outside. It can also be an outdoor space covered by a roof. We distinguish between two main construction systems:
- Solid construction: this element is composed of load-bearing structural layers which transfer the loads to vertical load-bearing elements (walls, columns), in certain cases via beams. The additional non-load-bearing layers complete the complex. These can have varying roles (insulation, waterproofing, vapour barrier, interior and exterior finishing, etc.).
- Lightweight construction: a framework of structural elements (beams, panels, trusses, rafters, sills, etc.) ensures the stability of the roof and transfers loads to vertical load-bearing elements. The non-framework roof complex generally consists of several layers, potentially with varying roles (insulation, waterproofing, vapour barrier, interior and exterior finishing, etc.). The frame members can be inside and/or outside the roof complex.
Other data sheets for slabs, frame elements and roof accessories: slab, lineair structural member, beam, column, chimney, gutter, roof finishing, ceiling finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Flat roof |  | IfcRoof.FLAT_ROOF | [5 empty] | IfcRoof.FLAT_ROOF |  | IfcRoof.FLAT_ROOF
Shed roof |  | IfcRoof.SHED_ROOF | [5 empty] | IfcRoof.SHED_ROOF |  | IfcRoof.SHED_ROOF
Gable roof |  | IfcRoof.GABLE_ROOF | [5 empty] | IfcRoof.GABLE_ROOF |  | IfcRoof.GABLE_ROOF
Hip roof |  | IfcRoof.HIP_ROOF | [5 empty] | IfcRoof.HIP_ROOF |  | IfcRoof.HIP_ROOF
Hipped gable roof |  | IfcRoof.HIPPED_GABLE_ROOF | [5 empty] | IfcRoof.HIPPED_GABLE_ROOF |  | IfcRoof.HIPPED_GABLE_ROOF
Gambrel roof |  | IfcRoof.GAMBREL_ROOF | [5 empty] | IfcRoof.GAMBREL_ROOF |  | IfcRoof.GAMBREL_ROOF
Mansard roof |  | IfcRoof.MANSARD_ROOF | [5 empty] | IfcRoof.MANSARD_ROOF |  | IfcRoof.MANSARD_ROOF
Barrel roof |  | IfcRoof.BARREL_ROOF | [5 empty] | IfcRoof.BARREL_ROOF |  | IfcRoof.BARREL_ROOF
Pavilion roof |  | IfcRoof.PAVILION_ROOF | [5 empty] | IfcRoof.PAVILION_ROOF |  | IfcRoof.PAVILION_ROOF
Dome roof |  | IfcRoof.DOME_ROOF | [5 empty] | IfcRoof.DOME_ROOF |  | IfcRoof.DOME_ROOF
Freeform |  | IfcRoof.FREEFORM | [5 empty] | IfcRoof.FREEFORM |  | IfcRoof.FREEFORM
Pergola |  | IfcRoof.NOTDEFINED | [5 empty] | IfcRoof.NOTDEFINED |  | IfcRoof.NOTDEFINED
In most cases, the various layers are modelled as a multilayer slab (IFcSlab – ROOF) for both solid and lightweight roofs. The frame elements are modelled separately (not systematic).
When exporting a roof, it is possible to export the roof as a whole with all its components (layers, profiles…), with the components as sub-entities of the global slab. It is also possible to decompose the roof on export, in which case each sub-component is an IFC element in its own right. The sub-components of a roof are:
- Overall solid roof: IfcSlab – ROOF or IfcRoof
- Overall lightweight roof: IfcRoof (including frame if applicable)
- Separated-out load-bearing layers: IfcSlab – ROOF
- Separate non-load-bearing layers IfcSlab – ROOF or IfcCovering (Ifc2x3 and Ifc4) – ROOFING – INSULATION – MEMBRANE – CEILING
- The frame can be composed of frame members (IfcMember), beams (IfcBeam) and columns (IfcColumn). The modelling of these elements is project-dependent and not systematic.
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Thickness | X
Perimeter | X
Slope | X
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
Slope |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Slope |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
Heat loss calculation
Thickness |  |  | X | X
Thickness of each layer |  |  | X | X
Reservations |  |  | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Slope |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope | X |  | X | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcElementAttributes.ShapeType |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_RoofCommon.Status1 |  | Pset_RoofCommon.Status |  | Pset_RoofCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing (Revit) | X |  | X | X | X | X | ePset_RoofCommon.LoadBearing1 |  | Pset_RoofCommon.LoadBearing |  | Pset_RoofCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_RoofCommon.IsExternal |  | Pset_RoofCommon.IsExternal |  | Pset_RoofCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | ePset_RoofCommon.ThermalTransmittance1 |  | Pset_RoofCommon.ThermalTransmittance |  | Pset_RoofCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_RoofCommon.FireRating |  | Pset_RoofCommon.FireRating |  | Pset_RoofCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | ePset_RoofCommon.ThermalTransmittance1 |  | Pset_RoofCommon.ThermalTransmittance |  | Pset_RoofCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | ePset_RoofCommon.ThermalTransmittance1 |  | Pset_RoofCommon.ThermalTransmittance |  | Pset_RoofCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | ePset_RoofCommon.ThermalTransmittance1 |  | Pset_RoofCommon.ThermalTransmittance |  | Pset_RoofCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  | X | X |  |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_RoofCommon.AcousticRating |  | Pset_RoofCommon.AcousticRating |  | Pset_RoofCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1020 – Roof Construction B3010 – Roofing B3040 – Traffic Bearing Horizontal Enclosures B3080 – Overhead Exterior Enclosures C2050 – Ceiling Finishes F1020 – Special Construction
DIN276 |  | 361 – Dachkonstruktionen 363 – Dachbeläge 364 – Dachbekleidungen 365 – Elementierte Dachkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Roof

## Roof finishing
Roof finishing
Return to overview
General
This sheet contains all the finishing layers for roofs. These are always non-load bearing layers.
Generally, the layers are modelled as multi-layers and the IFC export keeps these multi-layered walls, including the finishes. However, in some cases it is useful to have separate layers, and it is in these cases that the present GID sheet should be used
- Spot finishing on a floor, e.g. parquet flooring on a partial area of a floor in a room in the middle of tiling, modelled with a single layer "slab" overlaying the general multi-layer slab.
- Need to have each layer separate in the IFC model (quantity extraction, work tracking by materials...). It is possible to break down the layers into individual objects when exporting IFC. Depending on the software you can specify an IFC class and type for each layer (PARTS Revit), the class is fixed in other software (Archicad, Allplan...).
- If the native modelling has been done layer by layer, then the mapping will have to be specified layer by layer, each layer being an independent IFC object.
Other related sheets : floor finishing, wall finishing, ceiling finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Stone cladding (marble, granite,etc.) |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
Cladding (metal, cassette, stone,etc.) |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
Roofing (slate, tile, zinc,etc.) |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
Metal tray |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
Sandwich panel |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
Battens |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Levelling screed |  | IfcCovering.ROOFING | [5 empty] | IfcCovering.ROOFING |  | IfcCovering.ROOFING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
Slope |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Slope |  |  |  | X | X
Peripheral profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Slope |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Handicap accessibility (partial requirements)
Slope |  |  | X | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_WallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Layout plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1020.20 – Roof deck, slab and sheathing
DIN276 |  | 363 – Dachbeläge
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Roof finishing

## Safety lighting
Safety lighting
Return to overview
General
An emergency light fixture serves to provide artificial lighting with the objective of guiding occupants in an emergency situation. It can include the light fixture itself but also the lamp(s), transformer, dimmers and other accessories.
Other data sheet relating to lighting: light fixture.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Emergency lighting |  | IfcLightFixtureType.USERDEFINED[SECURITYLIGHTING] | [5 empty] | IfcLightFixture.SECURITYLIGHTING |  | IfcLightFixture.SECURITYLIGHTING
Emergency exit unit |  | IfcLightFixtureType.USERDEFINED[SECURITYLIGHTING] | [5 empty] | IfcLightFixture.SECURITYLIGHTING |  | IfcLightFixture.SECURITYLIGHTING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Fire safety (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Electrical design (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X
Width |  |  |  |  | X
Height |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Intrusion and surveillance (partial requirements)
Symbol |  |  |  | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Height | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowTerminalTypeCommon.Status1 |  | Pset_LightFixtureTypeCommon.Status |  | Pset_LightFixtureTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Maintenance factor |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.MaintenanceFactor |  | Pset_LightFixtureTypeCommon.MaintenanceFactor |  | Pset_LightFixtureTypeCommon.MaintenanceFactor
Luminous flux3 |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Placement |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType
Electrical power |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Type of mounting |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
Direction of the emergency picto |  |  |  |  | X | X | Pset_LightFixtureTypeExitSign.PictogramEscapeDirection |  | Pset_LightFixtureTypeSecurityLighting.PictogramEscapeDirection |  | Pset_LightFixtureTypeSecurityLighting.PictogramEscapeDirection
Backup system |  |  |  |  | X | X | Pset_LightFixtureTypeExitSign.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem
Type of security lighting |  |  |  |  | X | X | ePset_LightFixtureTypeExitSign.SecurityLightType1 |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType
Intrusion and surveillance (partial requirements)
Luminous flux3 |  |  |  |  | X | X | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux |  | Pset_LampTypeCommon.ContributedLuminousFlux
Placement |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType |  | Pset_LightFixtureTypeCommon.LightFixturePlacingType
Electrical power |  |  |  |  | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Backup system |  |  |  |  | X | X | Pset_LightFixtureTypeExitSign.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem
Type of security lighting |  |  |  |  | X | X | ePset_LightFixtureTypeExitSign.SecurityLightType1 |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType
Electrical design (partial requirements)
Electrical power |  |  |  | X | X | X | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage |  | Pset_LightFixtureTypeCommon.TotalWattage
Type of mounting |  |  |  | X | X | X | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType |  | Pset_LightFixtureTypeCommon.LightFixtureMountingType
Voltage |  |  |  |  | X | X | Pset_ElectricalDeviceCommon.NominalVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage |  | Pset_ElectricalDeviceCommon.RatedVoltage
Backup system |  |  |  | X | X | X | Pset_LightFixtureTypeExitSign.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem
Type of security lighting |  |  |  | X | X | X | ePset_LightFixtureTypeExitSign.SecurityLightType1 |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType
Fire safety (partial requirements)
Direction of the emergency picto |  |  |  |  | X | X | Pset_LightFixtureTypeExitSign.PictogramEscapeDirection |  | Pset_LightFixtureTypeSecurityLighting.PictogramEscapeDirection |  | Pset_LightFixtureTypeSecurityLighting.PictogramEscapeDirection
Backup system |  |  |  | X | X | X | Pset_LightFixtureTypeExitSign.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem |  | Pset_LightFixtureTypeSecurityLighting.BackupSupplySystem
Type of security lighting |  |  |  | X | X | X | ePset_LightFixtureTypeExitSign.SecurityLightType1 |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType
Handicap accessibility (partial requirements)
Type of security lighting |  |  |  | X | X | X | ePset_LightFixtureTypeExitSign.SecurityLightType1 |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType |  | Pset_LightFixtureTypeSecurityLighting.SecurityLightingType
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
3) Relates to another IFC class (IfcLamp)
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D5040.50 – Lighting Fixtures
DIN276 |  | KG445 – Beleuchtungsanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Safety lighting

## Sanitary equipment
Sanitary equipment
Return to overview
General
A sanitary equipment item is a device connected to the water supply network and generally also to the water drainage network. This data sheet covers a long list of devices, such as bidet, toilet bowl, toilet flush, shower tray, bath, sink, water fountain, urinal, hand basin etc.
Other related sheets : pump, tank, sanitary/heating pipe.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Bath |  | IfcSanitaryTerminalType.BATH | [5 empty] | IfcSanitaryTerminal.BATH |  | IfcSanitaryTerminal.BATH
Bidet |  | IfcSanitaryTerminalType.BIDET | [5 empty] | IfcSanitaryTerminal.BIDET |  | IfcSanitaryTerminal.BIDET
Flush |  | IfcSanitaryTerminalType.CISTERN | [5 empty] | IfcSanitaryTerminal.CISTERN |  | IfcSanitaryTerminal.CISTERN
Toilet bowl |  | IfcSanitaryTerminalType.TOILETPAN | [5 empty] | IfcSanitaryTerminal.TOILETPAN |  | IfcSanitaryTerminal.TOILETPAN
WC |  | IfcSanitaryTerminalType.TOILETPAN | [5 empty] | IfcSanitaryTerminal.TOILETPAN |  | IfcSanitaryTerminal.TOILETPAN
Toilet |  | IfcSanitaryTerminalType.TOILETPAN | [5 empty] | IfcSanitaryTerminal.TOILETPAN |  | IfcSanitaryTerminal.TOILETPAN
Dry toilet |  | IfcSanitaryTerminalType.TOILETPAN | [5 empty] | IfcSanitaryTerminal.TOILETPAN |  | IfcSanitaryTerminal.TOILETPAN
Sink |  | IfcSanitaryTerminalType.SINK | [5 empty] | IfcSanitaryTerminal.SINK |  | IfcSanitaryTerminal.SINK
Water fountain |  | IfcSanitaryTerminalType.SANITARYFOUNTAIN | [5 empty] | IfcSanitaryTerminal.SANITARYFOUNTAIN |  | IfcSanitaryTerminal.SANITARYFOUNTAIN
Hand wash basin |  | IfcSanitaryTerminalType.WASHHANDBASIN | [5 empty] | IfcSanitaryTerminal.WASHHANDBASIN |  | IfcSanitaryTerminal.WASHHANDBASIN
Shower tray |  | IfcSanitaryTerminalType.SHOWER | [5 empty] | IfcSanitaryTerminal.SHOWER |  | IfcSanitaryTerminal.SHOWER
Urinal |  | IfcSanitaryTerminalType.URINAL | [5 empty] | IfcSanitaryTerminal.URINAL |  | IfcSanitaryTerminal.URINAL
Washbasin |  | IfcSanitaryTerminalType.SINK | [5 empty] | IfcSanitaryTerminal.SINK |  | IfcSanitaryTerminal.SINK
A sanitary equipment can be composed of several components, e.g. shower tray, wall, mixer tap, stopcocks... When exporting a sanitary equipment, the Ifc entity can group all subcomponents or subcomponents can be separate Ifc objects :
- IfcFlowController (IFC2x3) et IfcValve (IFC4) – FAUCET – FLUSHING…
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Architectural design (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Maintenance (partial requirements)
Symbol |  |  |  |  | X | X
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Acoustics (partial requirements)
Height |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_FlowTerminalTypeCommon.Status1 |  | Pset_SanitaryTerminalTypeCommon.Status |  | Pset_SanitaryTerminalTypeCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | ePset_SanitaryTerminalTypeCommon.Status1 |  | Pset_SanitaryTerminalTypeCommon.Status |  | Pset_SanitaryTerminalTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Has tray |  |  |  |  | X | X | Pset_SanitaryTerminalTypeShower.HasTray |  | Pset_SanitaryTerminalTypeShower.HasTray |  | Pset_SanitaryTerminalTypeShower.HasTray
Capacity flush (volume) |  |  |  |  | X | X | Pset_SanitaryTerminalTypeCistern.CisternCapacity |  | Pset_SanitaryTerminalTypeCistern.CisternCapacity |  | Pset_SanitaryTerminalTypeCistern.CisternCapacity
Flush type |  |  |  |  | X | X | Pset_SanitaryTerminalTypeCistern.FlushType |  | Pset_SanitaryTerminalTypeCistern.FlushType |  | Pset_SanitaryTerminalTypeCistern.FlushType
Is automatic |  |  |  |  | X | X | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush |  | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush |  | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush
Sanitary/HVAC design (partial requirements)
Capacity flush (volume) |  |  |  | X | X | X | Pset_SanitaryTerminalTypeCistern.CisternCapacity |  | Pset_SanitaryTerminalTypeCistern.CisternCapacity |  | Pset_SanitaryTerminalTypeCistern.CisternCapacity
Flush type |  |  |  | X | X | X | Pset_SanitaryTerminalTypeCistern.FlushType |  | Pset_SanitaryTerminalTypeCistern.FlushType |  | Pset_SanitaryTerminalTypeCistern.FlushType
Is automatic |  |  |  | X | X | X | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush |  | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush |  | Pset_SanitaryTerminalTypeCistern.IsAutomaticFlush
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D2010.60 – Plumbing Fixtures
DIN276 |  | KG 412 – Wasseranlagen KG 473 – Medienversorgungsanlagen, Medizin- und labortechnische Anlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Sanitary equipment

## Sanitaryheating pipe
Sanitary/heating pipe
Return to overview
General
A pipe is an element of generally circular section along which flows a fluid, liquid, gas or solid in powder form, under pressure or not, in certain cases by gravity. A pipe can be flexible or rigid and generally belongs to a network. Uses include water supply (city water, rainwater, grey water), energy distribution (water/steam for heating or cooling), fire extinguishing distribution, sanitation (roof water downpipe, water waste, buried sewer, drainage…), fuel distribution network (oil, gas…), centralised vacuum cleaning system, fountains and plant watering…
Other related sheets : sanitary/heating pipe fitting, water collector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Rigid pipe |  | IfcPipeSegmentType.RIGIDSEGMENT | [5 empty] | IfcPipeSegment.RIGIDSEGMENT |  | IfcPipeSegment.RIGIDSEGMENT
Flexible pipe |  | IfcPipeSegmentType.FLEXIBLESEGMENT | [5 empty] | IfcPipeSegment.FLEXIBLESEGMENT |  | IfcPipeSegment.FLEXIBLESEGMENT
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
PEB (partial requirements)
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
2D documents (partial requirements)
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Slope |  |  |  |  | X | X
Insulation - thickness |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowSegmentTypeCommon.Status1 |  | Pset_PipeSegmentTypeCommon.Status |  | Pset_PipeSegmentTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B3020.70 Rainwater Management D2010.40 – Domestic Water Piping D2020.30 – Sanitary Sewerage Piping D2030.20 – Stormwater Drainage Piping D2030.60 – Grey Water Systems D2050 – General service Compressed-Air D2060.20 – Vacuum Systems D2060.30 – Gas Systems D2060.40 Chemical-Waste Systems D2060.50 Processed Water System D3010.10 Fuel Piping D3020.70 – Decentralized Heating Equipement D3030.10 – Central Cooling D3050.10 – Facility HVAC Distribution Systems D3050.30 – Facility Steam Distribution D3070.10 – Snow Melting D4010.10 – Water-Based Fire-Suppression D4010.50 – Fire-Extinguishing D5080.40 Cathodic Protection F1050.10 Pools F1050.20 Interior Fountains F1050.60 Ice Rinks G2060.10 Exterior Fountains G2080.10 – Planting Irrigation G3010.10 – Site Domestic Water Distribution G3010.30 – Site Fire Protection Water Distribution G3010.50 Site Irrigation Water Distribution G3020.20 Sanitary Sewerage Piping G3030.20 – Storm Drainage Piping G3030.30 – Culverts G3030.60 – Site Subdrainage G3050 – SIte Energy Distribution G3060 – Site Fuel Distribution G3090 – Liquid and Gas Site Utilities Supplementary Components
DIN276 |  | KG 326 – Dränagen KG 411 – Abwasseranlagen KG 412 – Wasseranlagen KG 413 – Gasanlagen KG 421 – Wärmeerzeugunganlagen KG 422 – Wärmeverteilnetze KG 431 – Lüftunganlagen KG 474 – Feuerlöschanlagen KG 484 – Kabel, Leitungen und Verlegesysteme
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.

## Sanitaryheating pipe fitting
Sanitary/heating pipe fitting
Return to overview
General
A pipe fitting includes, among others, elbows, section change adapters, T- and other-shaped fittings, and plugs. A fitting is part of a network composed of pipes (segments and fittings) of generally circular section intended for the flow of a fluid, liquid, gas or solid in powder form, under pressure or not, in certain cases by gravity. A pipe can be flexible or rigid. Types of networks include water supply (city water, rainwater, grey water), energy distribution (water/steam for heating or cooling), fire extinguishing substance distribution, sanitation (roof water downpipe, water waste, buried sewer, drainage…), fuel distribution network (oil, gas…), centralised vacuum cleaning system, fountains and plant watering…
Other sheet for pipes: sanitary/heating pipe, water collector.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Plug |  | IfcPipeFittingType.OBSTRUCTION | [5 empty] | IfcPipeFitting.OBSTRUCTION |  | IfcPipeFitting.OBSTRUCTION
Elbow |  | IfcPipeFittingType.BEND | [5 empty] | IfcPipeFitting.BEND |  | IfcPipeFitting.BEND
Shutter |  | IfcPipeFittingType.OBSTRUCTION | [5 empty] | IfcPipeFitting.OBSTRUCTION |  | IfcPipeFitting.OBSTRUCTION
Reducer |  | IfcPipeFittingType.TRANSITION | [5 empty] | IfcPipeFitting.TRANSITION |  | IfcPipeFitting.TRANSITION
Transition (section change) |  | IfcPipeFittingType.TRANSITION | [5 empty] | IfcPipeFitting.TRANSITION |  | IfcPipeFitting.TRANSITION
Junction (Y - T - X) |  | IfcPipeFittingType.JUNCTION | [5 empty] | IfcPipeFitting.JUNCTION |  | IfcPipeFitting.JUNCTION
Water manifold |  | IfcPipeFittingType.USERDEFINED[MANIFOLD] | [5 empty] | IfcPipeFitting.USERDEFINED[MANIFOLD] |  | IfcPipeFitting.USERDEFINED[MANIFOLD]
Heating manifold |  | IfcPipeFittingType.USERDEFINED[MANIFOLD] | [5 empty] | IfcPipeFitting.USERDEFINED[MANIFOLD] |  | IfcPipeFitting.USERDEFINED[MANIFOLD]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
PEB (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Slope |  |  |  |  | X | X
Insulation - thickness |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Slope |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowFittingTypeCommon.Status1 |  | Pset_PipeFittingTypeCommon.Status |  | Pset_PipeFittingTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B3020.70 Rainwater Management D2010.40 – Domestic Water Piping D2020.30 – Sanitary Sewerage Piping D2030.20 – Stormwater Drainage Piping D2030.60 – Grey Water Systems D2050 – General service Compressed-Air D2060.20 – Vacuum Systems D2060.30 – Gas Systems D2060.40 Chemical-Waste Systems D2060.50 Processed Water System D3010.10 Fuel Piping D3020.70 – Decentralized Heating Equipement D3030.10 – Central Cooling D3050.10 – Facility HVAC Distribution Systems D3050.30 – Facility Steam Distribution D3070.10 – Snow Melting D4010.10 – Water-Based Fire-Suppression D4010.50 – Fire-Extinguishing D5080.40 Cathodic Protection F1050.10 Pools F1050.20 Interior Fountains F1050.60 Ice Rinks G2060.10 Exterior Fountains G2080.10 – Planting Irrigation G3010.10 – Site Domestic Water Distribution G3010.30 – Site Fire Protection Water Distribution G3010.50 Site Irrigation Water Distribution G3020.20 Sanitary Sewerage Piping G3030.20 – Storm Drainage Piping G3030.30 – Culverts G3030.60 – Site Subdrainage G3050 – SIte Energy Distribution G3060 – Site Fuel Distribution G3090 – Liquid and Gas Site Utilities Supplementary Components
DIN276 |  | KG 326 – Dränagen KG 411 – Abwasseranlagen KG 412 – Wasseranlagen KG 413 – Gasanlagen KG 421 – Wärmeerzeugunganlagen KG 422 – Wärmeverteilnetze KG 431 – Lüftunganlagen KG 474 – Feuerlöschanlagen KG 484 – Kabel, Leitungen und Verlegesysteme
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Sanitary/heating pipe fitting

## Slab
Slab
Return to overview
General
A slab or floor is a normally horizontal surface element that partitions the spaces of a building (interior space/exterior space) horizontally. This element is composed of load-bearing structural layers which transfer the loads to vertical load-bearing elements (walls, columns), in certain cases via beams.
The non-load-bearing layers of the slab can have different roles:
- Insulation
- Waterproofing
- Interior or exterior finishing
- Base layer
- Other…
Other data sheets for floors, slabs and roofs: salb-on-grade, ramp, roof, stairs, technical floor, suspended ceiling, floor finishing.
Note that a roof can be represented by a slab (IfcSlab – ROOF) or by a roof (IfcRoof).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Load bearing slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Balcony |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Landing |  | IfcSlab.LANDING | [5 empty] | IfcSlab.LANDING |  | IfcSlab.LANDING
Load-bearing floor |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Roof |  | IfcSlab.ROOF | [5 empty] | IfcSlab.ROOF |  | IfcSlab.ROOF
Hollowcore |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Concrete topping |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Compression concrete layer |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Concrete pre-slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Rib and block slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Hollow block slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
Composite slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
TT slab |  | IfcSlab.FLOOR | [5 empty] | IfcSlab.FLOOR |  | IfcSlab.FLOOR
When exporting a slab, it is possible to export the slab as a whole with all its components (layers, profiles…), with the components as sub-entities of the global slab. It is also possible to decompose the slab on export, in which case each sub-component is an IFC element in its own right. The sub-components of a slab are:
- Global slab: IfcSlab
- Separated-out load-bearing layers: IfcSlab – FLOOR – ROOF – LANDING
- Non-load-bearing separated-out layers IfcSlab or IfcCovering (Ifc2x3 and Ifc4) – CEILING – FLOORING – ROOFING – INSULATION – MEMBRANE
- Skirting board, cornice…: IfcCovering (Ifc2x3 and Ifc4) – SKIRTINGBOARD – MOLDING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Steel reinforcement - dimensions |  |  |  |  | X
Reservations |  |  |  | X |  | X
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
Slope |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Slope |  |  |  | X | X
Peripheral profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Heat loss calculation
Thickness |  |  | X | X
Thickness of each layer |  |  | X | X
Reservations |  |  | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Slope |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Fire safety (partial requirements)
Perimeter | X |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_SlabCommon.Status1 |  | Pset_SlabCommon.Status |  | Pset_SlabCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing | X |  | X | X | X | X | Pset_SlabCommon.LoadBearing |  | Pset_SlabCommon.LoadBearing |  | Pset_SlabCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_SlabCommon.IsExternal |  | Pset_SlabCommon.IsExternal |  | Pset_SlabCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_SlabCommon.FireRating |  | Pset_SlabCommon.FireRating |  | Pset_SlabCommon.FireRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  | X | X |  |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1010.20 – Floor Decks, Slabs, and Toppings B1010.30 – Balcony Floor Construction B1010.40 – Mezzanine Floor Construction C2030 – Flooring C2050 – Ceiling Finishing
DIN276 |  | 351 – Deckenkonstruktionen 353 – Deckenbeläge 354 – Deckenbekleidungen 355 – Elementierte Deckenkonstruktionen 363 – Dachbeläge 364 – Dachbegleidungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Slab (load-bearing)

## Slab-on-grade
Slab-on-grade
Return to overview
General
A ground slab is a horizontal constructive element which is placed on the ground in sub-layers (insulation, waterproofing, draining stones, etc.). A distinction is made between load-bearing and non-load-bearing ground slabs
- A load-bearing ground slab, called a foundation raft or mat, is a direct foundation of the platform type made of reinforced concrete. This system permits the distribution of the loads on unstable ground (within certain limits) and serves to reduce the solicitation of the ground by increasing the solicited surface. This solution also serves to limit differential settlements on uneven ground. The construction of a raft requires a preliminary reinforced concrete study, with verification of the general settlement of the construction.
- A non-load-bearing ground slab is not intended to transmit the loads of the building (with the exception of its own load and that of its use transmitted directly to the ground).
The non-load-bearing layers of the slab can have different roles :
- Insulation
- Waterproofing
- Interior or exterior finishing
- Under-layer
- Other...
Other data sheets for direct foundations : foundation footing.
Other data sheets for essentially horizontal surface construction elements : slab, ramp, roof, stairs, floor finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Slab-on-grade |  | IfcSlab.BASESLAB | [5 empty] | IfcSlab.BASESLAB |  | IfcSlab.BASESLAB
Baseslab |  | IfcSlab.BASESLAB | [5 empty] | IfcSlab.BASESLAB |  | IfcSlab.BASESLAB
Paving |  | IfcSlab.BASESLAB | [5 empty] | IfcSlab.BASESLAB |  | IfcSlab.BASESLAB
When exporting a slab, it is possible to export the slab as a whole with all its components (layers, profiles…), with the components as sub-entities of the global slab. It is also possible to decompose the slab on export, in which case each sub-component is an IFC element in its own right. The sub-components of a slab are:
- Global slab: IfcSlab - BASESLAB
- Separated-out load-bearing layers: IfcSlab - FLOOR - ROOF - LANDING
- Separated-out non-load-bearing layers (under layer, screed, finish, etc.): IfcSlab or IfcCovering (Ifc2x3 and Ifc4) - CEILING - FLOORING - ROOFING - INSULATION - MEMBRANE
- Skirting board, cornice…: IfcCovering (Ifc2x3 and Ifc4) - SKIRTINGBOARD - MOLDING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
Slope |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Slope |  |  | X | X | X | X
2D documents (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  |  |  | X
Slope |  |  |  |  | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Thickness | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Slope |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Fire safety (partial requirements)
Perimeter | X |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_SlabCommon.Status1 |  | Pset_SlabCommon.Status |  | Pset_SlabCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing | X |  | X | X | X | X | Pset_SlabCommon.LoadBearing |  | Pset_SlabCommon.LoadBearing |  | Pset_SlabCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_SlabCommon.IsExternal |  | Pset_SlabCommon.IsExternal |  | Pset_SlabCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance |  | Pset_SlabCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Specific elements plan |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Geotechnical study report | X |  | X | X | X | X
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A4010 – Standard Slabs-on-Grade A4020 – Structural Slabs-on-Grade C2030 Flooring
DIN276 |  | 322 – Flachgründungen und Bodenplatten 324 – Gründungsbeläge 325 – Abdichtungen und Bekleidungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Slab-on-grade

## Solar panel
Solar panel
Return to overview
General
A solar collector converts solar energy into another energy form: electricity from photovoltaic panels and heat from solar thermal panels. There are also hybrid panels combining the two technologies in a single panel.
Solar thermal panels can be flat-plate or consist of vacuum tubes.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Solar panel |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARCOLLECTOR |  | IfcSolarDevice.SOLARCOLLECTOR
Solar thermal collector |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARCOLLECTOR |  | IfcSolarDevice.SOLARCOLLECTOR
Solar collector |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARCOLLECTOR |  | IfcSolarDevice.SOLARCOLLECTOR
Photovoltaic module |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARPANEL |  | IfcSolarDevice.SOLARPANEL
Photovoltaic panel |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARPANEL |  | IfcSolarDevice.SOLARPANEL
Hybrid solar panel |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.USERDEFINED[HYBRID] |  | IfcSolarDevice.USERDEFINED[HYBRID]
Tracker |  | IfcEnergyConversionDevice | [5 empty] | IfcSolarDevice.SOLARPANEL |  | IfcSolarDevice.SOLARPANEL
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Electrical design (partial requirements)
Symbol | X
Length |  |  | X | X | X
Width |  |  | X | X | X
Thickness |  |  | X | X | X
Slope |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Slope |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Thickness |  |  | X
Slope |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length | [5 empty] | X
Width | [5 empty] | X
Thickness | [5 empty] | X
Slope | [5 empty] | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Slope |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_EnergyConversionDeviceTypeCommon.Status1 |  | Pset_SolarDeviceTypeCommon.Status |  | Pset_SolarDeviceTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3020.10 – Heat Generation D5010.30 – Photovoltaic Collectors
DIN276 |  | KG 421 – Wärmeerzeugunganlagen KG 442 – Eigenstromversorgunganlagen KG 475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Solar panel

## Space
Space
Return to overview
General
A space represents a surface or a volume bounded physically by walls and/or theoretically by virtual planes (without physical walls). A space can be inside or outside. The division into spaces may vary from case to case: discipline, properties to be entered, gross or net surface/volume/with/without walls… We generally define its boundaries according to destination and use in an architectural model (use case 3) and by performance requirements in a technical systems model (use case 5): for example setpoint temperature, pulse or air extraction… It is preferable when possible to use the same boundary definition for the different disciplines.
Other data sheets for spatial organisation : site, building, MEP space, zone.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Room |  | IfcSpace | [5 empty] | IfcSpace |  | IfcSpace
Parking |  | IfcSpace.USERDEFINED[PARKING] | [5 empty] | IfcSpace.PARKING |  | IfcSpace.PARKING
At IFC level, there can be overlaps between different spaces (the net inside spaces on one hand and the raw spaces on the other hand largely overlap), however some software does not permit this.
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Programming (partial requirements)
Height | X
Perimeter | X
Building permit (partial requirements)
Height |  |  | X
Perimeter |  |  | X
PEB (partial requirements)
Height |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
2D documents (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Heat loss calculation
Height | X |  | X | X
Perimeter | X |  | X | X
Fire safety (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Architectural design (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Maintenance (partial requirements)
Height |  |  |  |  | X | X
Perimeter |  |  |  |  | X | X
Acoustics (partial requirements)
Height |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Rendering (partial requirements)
Perimeter | X |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Space name | X |  | X | X | X | X | IfcLongName. |  | IfcLongName. |  | IfcLongName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | BIMids_Common.Status1 |  | BIMids_Common.Status1 |  | BIMids_Common.Status1
Is external | X |  | X | X | X | X | ePset_SpaceCommon.IsExternal2 |  | ePset_SpaceCommon.IsExternal2 |  | Pset_SpaceCommon.IsExternal
Optional requirements
Space number | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1
Skirtingboard finishing |  |  |  | X | X | X | Pset_SpaceCommon.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard
Wall finishing |  |  |  | X | X | X | Pset_SpaceCommon.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering
Ceiling finishing |  |  |  | X | X | X | Pset_SpaceCommon.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering
Floor finishing |  |  |  | X | X | X | Pset_SpaceCommon.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering
Wall covering thickness |  |  |  | X | X | X | ePset_SpaceCoveringRequirements.WallCoveringThickness2 |  | Pset_SpaceCoveringRequirements.WallCoveringThickness |  | Pset_SpaceCoveringRequirements.WallCoveringThickness
Building permit (partial requirements)
Is handicap accessible |  |  | X |  |  |  | Pset_SpaceCommon.HandicapAccessible |  | Pset_SpaceCommon.HandicapAccessible |  | Pset_SpaceCommon.HandicapAccessible
Is public accessible |  |  | X |  |  |  | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible
Skirtingboard finishing3 |  |  | X |  |  |  | Pset_SpaceCommon.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard
Wall finishing3 |  |  | X |  |  |  | Pset_SpaceCommon.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering
Ceiling finishing3 |  |  | X |  |  |  | Pset_SpaceCommon.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering
Floor finishing3 |  |  | X |  |  |  | Pset_SpaceCommon.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering
Occupancy type |  |  | X |  |  |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Is emergency exit area |  |  | X |  |  |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit
Handicap accessibility (partial requirements)
Is handicap accessible | X |  | X | X | X | X | Pset_SpaceCommon.HandicapAccessible |  | Pset_SpaceCommon.HandicapAccessible |  | Pset_SpaceCommon.HandicapAccessible
Access management (partial requirements)
Is public accessible |  |  |  | X | X | X | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible
Occupancy number |  |  |  | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type |  |  |  | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Is emergency exit area |  |  |  | X | X | X | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit
Fire safety (partial requirements)
Is public accessible | X |  | X | X | X | X | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible |  | Pset_SpaceCommon.PubliclyAccessible
Occupancy number |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Is emergency exit area |  |  | X | X | X | X | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit
Fire risk factor |  |  | X | X | X | X | Pset_SpaceFireSafetyRequirements.FireRiskFactor |  | Pset_SpaceFireSafetyRequirements.FireRiskFactor |  | Pset_SpaceFireSafetyRequirements.FireRiskFactor
Has sprinklers |  |  | X | 4 | 4 | 4 | Pset_SpaceFireSafetyRequirements.SprinklerProtection |  | Pset_SpaceFireSafetyRequirements.SprinklerProtection |  | Pset_SpaceFireSafetyRequirements.SprinklerProtection
Architectural design (partial requirements)
Skirtingboard finishing3 |  |  | X | X | X | X | Pset_SpaceCommon.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard
Wall finishing3 |  |  | X | X | X | X | Pset_SpaceCommon.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering
Ceiling finishing3 |  |  | X | X | X | X | Pset_SpaceCommon.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering
Floor finishing3 |  |  | X | X | X | X | Pset_SpaceCommon.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering
Minimum headroom | X |  | X | X | X |  | Pset_SpaceOccupancyRequirements.MinimumHeadroom |  | Pset_SpaceOccupancyRequirements.MinimumHeadroom |  | Pset_SpaceOccupancyRequirements.MinimumHeadroom
Occupancy number |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Acoustics (partial requirements)
Skirtingboard finishing3 |  |  |  | X | X | X | Pset_SpaceCommon.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard |  | Pset_SpaceCoveringRequirements.SkirtingBoard
Wall finishing3 |  |  |  | X | X | X | Pset_SpaceCommon.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering
Ceiling finishing3 |  |  |  | X | X | X | Pset_SpaceCommon.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering
Floor finishing3 |  |  |  | X | X | X | Pset_SpaceCommon.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering
Occupancy number |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Maintenance (partial requirements)
Wall finishing3 |  |  |  |  | X | X | Pset_SpaceCommon.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering |  | Pset_SpaceCoveringRequirements.WallCovering
Ceiling finishing3 |  |  |  |  | X | X | Pset_SpaceCommon.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering |  | Pset_SpaceCoveringRequirements.CeilingCovering
Floor finishing3 |  |  |  |  | X | X | Pset_SpaceCommon.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering |  | Pset_SpaceCoveringRequirements.FloorCovering
Minimum headroom |  |  |  |  | X | X | Pset_SpaceOccupancyRequirements.MinimumHeadroom |  | Pset_SpaceOccupancyRequirements.MinimumHeadroom |  | Pset_SpaceOccupancyRequirements.MinimumHeadroom
Occupancy number |  |  |  |  | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type |  |  |  |  | X | X | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Is emergency exit area |  |  |  |  | X | X | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit
Fire risk factor |  |  |  |  | X | X | Pset_SpaceFireSafetyRequirements.FireRiskFactor |  | Pset_SpaceFireSafetyRequirements.FireRiskFactor |  | Pset_SpaceFireSafetyRequirements.FireRiskFactor
Has sprinklers |  |  |  | 4 | X | X | Pset_SpaceFireSafetyRequirements.SprinklerProtection |  | Pset_SpaceFireSafetyRequirements.SprinklerProtection |  | Pset_SpaceFireSafetyRequirements.SprinklerProtection
Required illumination |  |  |  |  | X | X | ePset_SpaceLightingRequirements.Illuminance2 |  | Pset_SpaceLightingRequirements.Illuminance |  | Pset_SpaceLightingRequirements.Illuminance
Humidity winter (heating) |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceHumidityWinter |  | Pset_SpaceThermalRequirements.SpaceHumidityWinter |  | Pset_SpaceThermalRequirements.SpaceHumidityWinter
Humidity summer (cooling) |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceHumiditySummer |  | Pset_SpaceThermalRequirements.SpaceHumiditySummer |  | Pset_SpaceThermalRequirements.SpaceHumiditySummer
Maximum heating temperature |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax
Maximum cooling temperature |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax
Minimum cooling temperature |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin
Minimum heating temperature |  |  |  |  | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin
Mechanical ventilation required |  |  |  |  | X | X | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate
Required natural ventilation |  |  |  |  | X | X | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate
Programming (partial requirements)
Occupancy number | X | [5 empty] | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type | X | [5 empty] | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Net programmed area | X | [5 empty] | Pset_SpaceCommon.NetPlannedArea |  | Pset_SpaceCommon.NetPlannedArea |  | Pset_SpaceCommon.NetPlannedArea
PEB (partial requirements)
Occupancy number |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type |  |  | X | X | X | X | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Maximum heating temperature |  |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMax
Maximum cooling temperature |  |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMax
Minimum cooling temperature |  |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureSummerMin
Minimum heating temperature |  |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin |  | Pset_SpaceThermalRequirements.SpaceTemperatureWinterMin
Mechanical ventilation required |  |  | X | X | X | X | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate
Required natural ventilation |  |  | X | X | X | X | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate
Heat loss calculation
Occupancy number | X |  | X | X |  |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber |  | Pset_SpaceOccupancyRequirements.OccupancyNumber
Occupancy type | X |  | X | X |  |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType |  | Pset_SpaceOccupancyRequirements.OccupancyType
Intrusion and surveillance (partial requirements)
Is emergency exit area |  |  | X | X | X | X | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit |  | Pset_SpaceFireSafetyRequirements.FireExit
Electrical design (partial requirements)
Required illumination | X |  | X | X | X | X | ePset_SpaceLightingRequirements.Illuminance2 |  | Pset_SpaceLightingRequirements.Illuminance |  | Pset_SpaceLightingRequirements.Illuminance
Sanitary/HVAC design (partial requirements)
Humidity winter (heating) | X |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceHumidityWinter |  | Pset_SpaceThermalRequirements.SpaceHumidityWinter |  | Pset_SpaceThermalRequirements.SpaceHumidityWinter
Humidity summer (cooling) | X |  | X | X | X | X | Pset_SpaceThermalRequirements.SpaceHumiditySummer |  | Pset_SpaceThermalRequirements.SpaceHumiditySummer |  | Pset_SpaceThermalRequirements.SpaceHumiditySummer
Mechanical ventilation required |  |  | X | X | X | X | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate |  | Pset_SpaceThermalRequirements.MechanicalVentilationRate
Required natural ventilation |  |  | X | X | X | X | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate |  | Pset_SpaceThermalRequirements.NaturalVentilationRate
1) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
2) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
3) Required only if not modelled in a layer or specific element.
4) see page "Sprinkler"
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Plans and diagrams
Space planning diagram | X
Reports
Energy report |  |  | X | X | X | X
Tables
Zone data sheet | X |  | X | X | X | X
List of rooms | X |  | X | X | X | X
Operating loads |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | None
DIN276 |  | None
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Sprinkler
Sprinkler
Return to overview
General
A sprinkler is a fixed automatic water extinguishing installation that is self-activated in the event of excessive heat in a protected room or site during a fire. This system is networked and consists of extinguisher heads screwed onto pipes, connected to a control station which regulates the water supply.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Sprinkler |  | IfcFireSuppressionTerminalType.SPRINKLER | [5 empty] | IfcFireSuppressionTerminal.SPRINKLER |  | IfcFireSuppressionTerminal.SPRINKLER
Automatic water extinguisher |  | IfcFireSuppressionTerminalType.SPRINKLER | [5 empty] | IfcFireSuppressionTerminal.SPRINKLER |  | IfcFireSuppressionTerminal.SPRINKLER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol |  |  | X1
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Fire safety (partial requirements)
Symbol |  |  | X1
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Symbol |  |  |  |  | X
Clash detection (partial requirements)
Symbol |  |  | X1
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Rendering (partial requirements)
Length |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
1) See page "Space"
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeCommon.Status |  | Pset_FireSuppressionTerminalTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_FireSuppressionTerminalTypeCommon.Status1 |  | Pset_FireSuppressionTerminalTypeSprinkler.Status |  | Pset_FireSuppressionTerminalTypeSprinkler.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type of sprinkler |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType |  | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType |  | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType
Type activation |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeSprinkler.Activation |  | Pset_FireSuppressionTerminalTypeSprinkler.Activation |  | Pset_FireSuppressionTerminalTypeSprinkler.Activation
Activation temperature |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature |  | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature |  | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature
Covered area |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea |  | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea |  | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea
Has diffuser |  |  |  |  | X | X | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector |  | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector |  | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector
Fire safety (partial requirements)
Type of sprinkler |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType |  | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType |  | Pset_FireSuppressionTerminalTypeSprinkler.SprinklerType
Type activation |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeSprinkler.Activation |  | Pset_FireSuppressionTerminalTypeSprinkler.Activation |  | Pset_FireSuppressionTerminalTypeSprinkler.Activation
Activation temperature |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature |  | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature |  | Pset_FireSuppressionTerminalTypeSprinkler.ActivationTemperature
Covered area |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea |  | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea |  | Pset_FireSuppressionTerminalTypeSprinkler.CoverageArea
Has diffuser |  |  |  | X | X | X | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector |  | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector |  | Pset_FireSuppressionTerminalTypeSprinkler.HasDeflector
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Communication protocol |  |  |  | X | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Plans and diagrams
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D4010 – Fire Suppression
DIN276 |  | KG474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Sprinkler

## Stair
Stair
Return to overview
General
A stair is a construction element set at an incline that connects spaces located at different levels, for foot access only. A staircase can consist of one or more flights separated by horizontal landings. A distinction is made between a staircase resting on the ground and a self-bearing staircase:
- A ground-based staircase is placed on the ground via sub-layers (insulation, sealing, draining stones). It is not intended to transmit the loads of the building (with the exception of its own load and that of its use transmitted directly to the ground).
- A load-bearing staircase partitions the spaces of a building horizontally (like a slab). This element is composed of a load-bearing structural part which transfers the loads to vertical load-bearing elements (walls, columns), in certain cases via beams.
Other linked sheets : roof finishing, ceiling finishing, floor finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Straight run stair |  | IfcStair.STRAIGHT_RUN_STAIR | [5 empty] | IfcStair.STRAIGHT_RUN_STAIR |  | IfcStair.STRAIGHT_RUN_STAIR
Twostraight run stair |  | IfcStair.TWO_STRAIGHT_RUN_STAIR | [5 empty] | IfcStair.TWO_STRAIGHT_RUN_STAIR |  | IfcStair.TWO_STRAIGHT_RUN_STAIR
Quarter winding stair |  | IfcStair.QUARTER_WINDING_STAIR | [5 empty] | IfcStair.QUARTER_WINDING_STAIR |  | IfcStair.QUARTER_WINDING_STAIR
Quarter turn stair |  | IfcStair.QUARTER_TURN_STAIR | [5 empty] | IfcStair.QUARTER_TURN_STAIR |  | IfcStair.QUARTER_TURN_STAIR
Half winding stair |  | IfcStair.HALF_WINDING_STAIR | [5 empty] | IfcStair.HALF_WINDING_STAIR |  | IfcStair.HALF_WINDING_STAIR
Half turn stair |  | IfcStair.HALF_TURN_STAIR | [5 empty] | IfcStair.HALF_TURN_STAIR |  | IfcStair.HALF_TURN_STAIR
Two quarter winding stair |  | IfcStair.TWO_QUARTER_WINDING_STAIR | [5 empty] | IfcStair.TWO_QUARTER_WINDING_STAIR |  | IfcStair.TWO_QUARTER_WINDING_STAIR
Two quarter turn stair |  | IfcStair.TWO_QUARTER_TURN_STAIR | [5 empty] | IfcStair.TWO_QUARTER_TURN_STAIR |  | IfcStair.TWO_QUARTER_TURN_STAIR
Three quarter winding stair |  | IfcStair.THREE_QUARTER_WINDING_STAIR | [5 empty] | IfcStair.THREE_QUARTER_WINDING_STAIR |  | IfcStair.THREE_QUARTER_WINDING_STAIR
Three quarter turn stair |  | IfcStair.THREE_QUARTER_TURN_STAIR | [5 empty] | IfcStair.THREE_QUARTER_TURN_STAIR |  | IfcStair.THREE_QUARTER_TURN_STAIR
Spiral stair |  | IfcStair.SPIRAL_STAIR | [5 empty] | IfcStair.SPIRAL_STAIR |  | IfcStair.SPIRAL_STAIR
Double return stair |  | IfcStair.DOUBLE_RETURN_STAIR | [5 empty] | IfcStair.DOUBLE_RETURN_STAIR |  | IfcStair.DOUBLE_RETURN_STAIR
Curved run stair |  | IfcStair.CURVED_RUN_STAIR | [5 empty] | IfcStair.CURVED_RUN_STAIR |  | IfcStair.CURVED_RUN_STAIR
Two curved run stair |  | IfcStair.TWO_CURVED_RUN_STAIR | [5 empty] | IfcStair.TWO_CURVED_RUN_STAIR |  | IfcStair.TWO_CURVED_RUN_STAIR
Free form stair |  | IfcStair.USERDEFINED[FREEFORM] | [5 empty] | IfcStair.USERDEFINED[FREEFORM] |  | IfcStair.USERDEFINED[FREEFORM]
he components of an IfcStair are:
- Flight (of stairs) and stringer: IfcStairFlight (IFC2x3 and IFC4) – STRAIGHT – WINDER – SPIRAL – CURVED – FREEFORM – USERDEFINED – NOTDEFINED
- Landing: IfcSlab – LANDING (see slab)
- Railing: IfcRailing (IFC2x3 and IFC4) – HANDRAIL – GARDRAIL – BALUSTRADE – USERDEFINED – NOTDEFINED (A separate data sheet will be published later)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Structural design (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions |  |  | X | X | X | X
Building permit (partial requirements)
Flight - dimensions |  |  | X
Landing - dimensions |  |  | X
Railing - dimensions |  |  | X
Precasting (partial requirements)
Flight - dimensions |  |  |  | X | X
Landing - dimensions |  |  |  | X | X
Railing - dimensions |  |  |  | X | X
2D documents (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions | X |  | X | X | X | X
Fire safety (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Architectural design (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions | X |  | X | X | X | X
Handicap accessibility (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
LCA (Life Cycle Analysis)
Flight - dimensions |  |  | X |  | X
Landing - dimensions |  |  | X |  | X
Railing - dimensions |  |  | X |  | X
Acoustics (partial requirements)
Flight - dimensions |  |  | X | X | X | X
Landing - dimensions |  |  | X | X | X | X
Clash detection (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions | X |  | X | X | X | X
Rendering (partial requirements)
Flight - dimensions | X |  | X | X | X | X
Landing - dimensions | X |  | X | X | X | X
Railing - dimensions | X |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcElementAttributes.ShapeType |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | Pset_StairCommon.Status |  | Pset_StairCommon.Status |  | Pset_StairCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_StairCommon.Status |  | Pset_StairCommon.Status |  | Pset_StairCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external | X |  | X | X | X | X | Pset_StairCommon.IsExternal |  | Pset_StairCommon.IsExternal |  | Pset_StairCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage1 |  | BIMids_Common.WorkPackage1 |  | BIMids_Common.WorkPackage1
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell1 |  | BIMids_Common.OuterShell1 |  | BIMids_Common.OuterShell1
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity2 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_StairCommon.FireRating |  | Pset_StairCommon.FireRating |  | Pset_StairCommon.FireRating
Is emergency exit |  |  | X | X | X | X | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Access management (partial requirements)
Is emergency exit |  |  |  | X | X | X | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit
Intrusion and surveillance (partial requirements)
Is emergency exit |  |  | X | X | X | X | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit |  | Pset_StairCommon.FireExit
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance |  | Pset_StairCommon.ThermalTransmittance
Thermal conductivity |  |  | X |  |  |  | ePset_MaterialThermal.ThermalConductivity2 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell1 |  | BIMids_Common.OuterShell1 |  | BIMids_Common.OuterShell1
Architectural design (partial requirements)
Place of assembly |  |  |  | X | X | X | ePset_ManufacturerTypeInformation.AssemblyPlace2 |  | Pset_ManufacturerTypeInformation.AssemblyPlace |  | Pset_ManufacturerTypeInformation.AssemblyPlace
1) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
2) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B1080.10 – Stair Construction B1080.30 – Stair Soffits B1080.50 – Stair Railings C2040 – Stair Finishing E1060.50 – Residential Stairs
DIN276 |  | 324 – Gründungsbeläge 351 – Deckenkonstruktionen 353 – Deckenbeläge 355 – Elementierte Deckenkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Tank
Tank
Return to overview
General
A tank is a container generally used to store a fluid or gas for later use, under pressure or not (oil tank, rainwater tank, fire extinguishing water tank, gas tank, septic tank, grey water for treatment storage tank …). A tank can also service to regulate pressure in a network (expansion tank), to remove over-pressures (pressure breaker bottle), to store heat/cold (buffer tank, hot water tank, ice tank …).
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Fire fighting storage |  | IfcTankType.USERDEFINED[VESSEL] | [5 empty] | IfcTank.VESSEL |  | IfcTank.VESSEL
Buffer tank |  | IfcTankType.PRESSUREVESSEL | [5 empty] | IfcTank.PRESSUREVESSEL |  | IfcTank.PRESSUREVESSEL
Dead water tank |  | IfcTankType.USERDEFINED[VESSEL] | [5 empty] | IfcTank.VESSEL |  | IfcTank.VESSEL
Rain water harvesting |  | IfcTankType.USERDEFINED[BASIN] | [5 empty] | IfcTank.BASIN |  | IfcTank.BASIN
Retention tank |  | IfcTankType.USERDEFINED[BASIN] | [5 empty] | IfcTank.BASIN |  | IfcTank.BASIN
Pressure-breaking cylinder |  | IfcTankType.USERDEFINED[BREAKPRESSURE] | [5 empty] | IfcTank.BREAKPRESSURE |  | IfcTank.BREAKPRESSURE
Rainwater tank |  | IfcTankType.USERDEFINED[STORAGE] | [5 empty] | IfcTank.STORAGE |  | IfcTank.STORAGE
Grey water tank |  | IfcTankType.USERDEFINED[STORAGE] | [5 empty] | IfcTank.STORAGE |  | IfcTank.STORAGE
Septic tank |  | IfcTankType.USERDEFINED[STORAGE] | [5 empty] | IfcTank.STORAGE |  | IfcTank.STORAGE
Pressure tank (O2, CO2,etc.) |  | IfcTankType.PRESSUREVESSEL | [5 empty] | IfcTank.PRESSUREVESSEL |  | IfcTank.PRESSUREVESSEL
Expansion tank |  | IfcTankType.EXPANSION | [5 empty] | IfcTank.EXPANSION |  | IfcTank.EXPANSION
Oil tank |  | IfcTankType.USERDEFINED[STORAGE] | [5 empty] | IfcTank.STORAGE |  | IfcTank.STORAGE
Gas tank (natural gas, propane, etc.) |  | IfcTankType.PRESSUREVESSEL | [5 empty] | IfcTank.PRESSUREVESSEL |  | IfcTank.PRESSUREVESSEL
Sump |  | IfcTankType.USERDEFINED[STORAGE] | [5 empty] | IfcTank.STORAGE |  | IfcTank.STORAGE
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Symbol |  |  | X
2D documents (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Clash detection (partial requirements)
Symbol | X |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_FlowStotageDeviceTypeCommon.Status1 |  | Pset_TankTypeCommon.Status |  | Pset_TankTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Type of storage |  |  |  |  | X | X | ePset_TankTypeCommon.StorageType1 |  | Pset_TankTypeCommon.StorageType |  | Pset_TankTypeCommon.StorageType
Effective volume |  |  |  |  | X | X | ePset_TankTypeCommon.EffectiveCapacity1 |  | Pset_TankTypeCommon.EffectiveCapacity |  | Pset_TankTypeCommon.EffectiveCapacity
Nominal volume |  |  |  |  | X | X | ePset_TankTypeCommon.NominalCapacity1 |  | Pset_TankTypeCommon.NominalCapacity |  | Pset_TankTypeCommon.NominalCapacity
Sanitary/HVAC design (partial requirements)
Type of storage |  |  | X | X | X | X | ePset_TankTypeCommon.StorageType1 |  | Pset_TankTypeCommon.StorageType |  | Pset_TankTypeCommon.StorageType
Effective volume |  |  |  |  | X | X | ePset_TankTypeCommon.EffectiveCapacity1 |  | Pset_TankTypeCommon.EffectiveCapacity |  | Pset_TankTypeCommon.EffectiveCapacity
Nominal volume |  |  |  | X | X | X | ePset_TankTypeCommon.NominalCapacity1 |  | Pset_TankTypeCommon.NominalCapacity |  | Pset_TankTypeCommon.NominalCapacity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D2010.10 – Facility Potable-Water Storage Tanks D2020.10 – Sanitary Sewerage Equipement D2030.10 – Stormwater Drainage Equipement D2030.60 – Grey Water Systems D2060.30 – Gas Systems D2060.40 – Chemical-Waste Systems D3010.50 – Fuel Storage Tanks D3050.10 – Facility Hydronic Distribution D3050.30 – Facility Steam Distribution D5080.40 – Cathodic Protection G1050.60 – Contaminated Site Material Removal G3010.10 – Site Domestic Water Distribution G3010.30 Site Fire Protection Water Distribution G3010.50 – SIte Irrigation Water Distribution G3020.40 – Utiilty Septic Tanks G3060 – Site Fuel Distribution
DIN276 |  | KG 412 – Wasseranlagen KG 413 – Gasanlagen KG 421 – Wärmeerzeugunganlagen KG 473 – Medienversorgsunganlagen, Medizin- und labortechnische Anlagen KG 474 – Feuerlöschanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Tank

## Technical floor
Technical floor
Return to overview
General
A technical floor or raised floor permits quick and easy access to the technical area under this floor, for adapting the technical installations to the changing needs of the premises.
The floor is generally composed of:
- adjustable support feet
- a single or crossed metal structure (if applicable)
- generally removable panels
- a floor covering (a priori easily removable such as carpet tiles)
Other related sheets : slab-on-grade, slab, suspended ceiling.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Technical floor |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | [5 empty] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
False floor |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | [5 empty] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Raised floor |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | [5 empty] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
Metal grating |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] | [5 empty] | IfcCovering.USERDEFINED[TECHNICAL_FLOOR] |  | IfcCovering.USERDEFINED[TECHNICAL_FLOOR]
When exporting a technical floor it is possible to export it as a whole with all its components (layers, profiles…), with the components as sub-entities of the global floor. It is also possible to decompose the floor on export, in which case each sub-component is an IFC element in its own right. The sub-components of a technical floor are:
- Global technical floor: IfcCovering – FLOORING (floor finishing)
- Floor panels (removable or not): IfcCovering – FLOORING (floor finishing)
- Sub-construction: IfcMember (frame member)
- Support: IfcMember (frame member) or IfcColumn (column)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Thickness |  |  | X
Thickness of each layer |  |  | X
Perimeter |  |  | X
PEB (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Precasting (partial requirements)
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Perimeter |  |  |  | X | X
Inspection trap door - dimensions |  |  |  | X | X
Reservations |  |  |  | X | X
Profile of structural elements - dimensions |  |  |  | X | X
2D documents (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
Architectural design (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
LCA (Life Cycle Analysis)
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Perimeter |  |  | X |  | X
Maintenance (partial requirements)
Thickness |  |  |  |  | X | X
Thickness of each layer |  |  |  |  | X | X
Perimeter |  |  |  |  | X | X
Inspection trap door - dimensions |  |  |  |  | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
Acoustics (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Profile of structural elements - dimensions |  |  |  |  | X | X
Rendering (partial requirements)
Thickness |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Inspection trap door - dimensions |  |  |  | X | X | X
Access management (partial requirements)
Inspection trap door - dimensions |  |  |  | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Profile of structural elements - dimensions |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Flammability rating | [5 empty] | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating
Thermal transmittance |  |  |  |  | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Acoustic resistance |  |  |  |  | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Flammability rating |  |  |  |  | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Thermal conductivity |  |  |  |  | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Heat loss calculation
Thermal conductivity |  |  | X | X |  |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Construction details |  |  |  | X | X | X
Tables
Operating loads |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | C1060.10 – Access Flooring C2030 – Flooring
DIN276 |  | KG 324 – Gründungsbeläge KG 353 – Deckenbeläge
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Technical floor

## Transport equipment (excluding
Transport equipment (excluding lifts)
Return to overview
General
Transport equipment serving to move persons or goods horizontally and/or vertically in a building, in particular escalators, mechanical ramps, lifting platforms, chutes, laundry chutes, conveyor belts, travelling cranes, façade gondolas, loading bridges, pneumatic conveyors…
Other related sheet : lift.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Stair lift |  | IfcTransportElement.USERDEFINED[STAIR_LIFT] | [5 empty] | IfcTransportElement.USERDEFINED[STAIR_LIFT] |  | IfcTransportElement.USERDEFINED[STAIR_LIFT]
Freight lift |  | IfcTransportElement.ELEVATOR | [5 empty] | IfcTransportElement.ELEVATOR |  | IfcTransportElement.ELEVATOR
Derrick (load mast) |  | IfcTransportElement.USERDEFINED[LIFTINGGEAR] | [5 empty] | IfcTransportElement.LIFTINGGEAR |  | IfcTransportElement.LIFTINGGEAR
Escalator |  | IfcTransportElement.ESCALATOR | [5 empty] | IfcTransportElement.ESCALATOR |  | IfcTransportElement.ESCALATOR
Rubble chute |  | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE] | [5 empty] | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE] |  | IfcTransportElement.USERDEFINED[RUBBLE_CHUTE]
Crane |  | IfcTransportElement.USERDEFINED[CRANEWAY] | [5 empty] | IfcTransportElement.CRANEWAY |  | IfcTransportElement.CRANEWAY
Facade gondola |  | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | [5 empty] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] |  | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM]
Lifting gear |  | IfcTransportElement.USERDEFINED[LIFTINGGEAR] | [5 empty] | IfcTransportElement.LIFTINGGEAR |  | IfcTransportElement.LIFTINGGEAR
Laundry chute |  | IfcTransportElement.USERDEFINED[LAUNDRY_PASS] | [5 empty] | IfcTransportElement.USERDEFINED[LAUNDRY_PASS] |  | IfcTransportElement.USERDEFINED[LAUNDRY_PASS]
Boarding bridge |  | IfcTransportElement.USERDEFINED[GATEWAY] | [5 empty] | IfcTransportElement.USERDEFINED[GATEWAY] |  | IfcTransportElement.USERDEFINED[GATEWAY]
Lifting platform |  | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] | [5 empty] | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM] |  | IfcTransportElement.USERDEFINED[LIFTING_PLATFORM]
Bridge crane |  | IfcTransportElement.USERDEFINED[CRANEWAY] | [5 empty] | IfcTransportElement.CRANEWAY |  | IfcTransportElement.CRANEWAY
Mechanical ramp |  | IfcTransportElement.MOVINGWALKWAY | [5 empty] | IfcTransportElement.MOVINGWALKWAY |  | IfcTransportElement.MOVINGWALKWAY
Pneumatic tube system |  | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | [5 empty] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] |  | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM]
Teletube |  | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] | [5 empty] | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM] |  | IfcTransportElement.USERDEFINED[PNEUMATIC_TUBE_SYSTEM]
Conveyor belt |  | IfcTransportElement.MOVINGWALKWAY | [5 empty] | IfcTransportElement.MOVINGWALKWAY |  | IfcTransportElement.MOVINGWALKWAY
Escape slide |  | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE] | [5 empty] | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE] |  | IfcTransportElement.USERDEFINED[ESCAPE_SLIDE]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
Fire safety (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Clash detection (partial requirements)
Symbol | X
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Maintenance intervention volume |  |  |  |  | X | X
Technical rooms - dimensions |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
Minimum requirements
Maintenance intervention volume |  |  | X | X | X | X
Technical rooms - dimensions |  |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_TransportElementCommon.Status1 |  | Pset_TransportElementCommon.Status |  | Pset_TransportElementCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Capacity in weight |  |  |  |  | X | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  |  |  | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Building permit (partial requirements)
Capacity in weight |  |  | X |  |  |  | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  | X |  |  |  | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Electrical design (partial requirements)
Capacity in weight |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityWeight1 |  | Pset_TransportElementCommon.CapacityWeight |  | Pset_TransportElementCommon.CapacityWeight
Capacity in persons |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
Handicap accessibility (partial requirements)
Capacity in persons |  |  | X | X | X | X | ePset_TransportElementCommon.CapacityPeople1 |  | Pset_TransportElementCommon.CapacityPeople |  | Pset_TransportElementCommon.CapacityPeople
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Construction details |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D1010.20 – Lifts D1010.30 – Escalators D1010.50 – Dumbwaiters D1030.10 – Movingwalkway D1030.30 – Turntables D1030.50 – Passenger Loading Bridges D1030.70 – People Movers (monorail-funicular-cable transportation) D1050.10 – Cranes D1050.20 – Hoists D1050.30 – Derricks D1050.40 – Conveyors D1050.50 – Baggage Handling Equipement D1050.60 – Chutes (coal chutes, escape chutes, laundry an linen chutes) D1050.70 – Pneumatic Tube Systems
DIN276 |  | KG 462 – Fahrtreppen, Fahrsteige KG 463 – Befahranlagen KG 464 – Transportanlagen KG 465 – Krananlagen KG 466 – Hydraulikanlagen KG469 – Sonstiges zur KG 460 (Förderanlagen)
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Ventilation air terminal
Ventilation air terminal
Return to overview
General
A vent is the origin or end point between an air distribution system and a space (room). A vent can have different shapes (linear, circular, rectangular), different directions of diffusion and additional functions (flow rate adjustment, etc.).
Other data sheets for ventilation elements: ventilation duct, ventilation duct connection, fan, filter, air handling unit, air-to-air exchanger.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Non adjustable vent diffuser |  | IfcAirTerminalType.DIFFUSER | [5 empty] | IfcAirTerminal.DIFFUSER |  | IfcAirTerminal.DIFFUSER
Adjustable vent diffuser |  | IfcAirTerminalType.REGISTER | [5 empty] | IfcAirTerminal.REGISTER |  | IfcAirTerminal.REGISTER
Linear grille |  | IfcAirTerminalType.LINEARGRILLE | [5 empty] | IfcAirTerminal.LOUVRE |  | IfcAirTerminal.LOUVRE
Grille |  | IfcAirTerminalType.GRILLE | [5 empty] | IfcAirTerminal.GRILLE |  | IfcAirTerminal.GRILLE
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Thickness |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Thickness |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_FlowTerminalTypeCommon.Status1 |  | Pset_AirTerminalTypeCommon.Status |  | Pset_AirTerminalTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Nominal air flow |  |  |  |  | X | X | Pset_AirTerminalTypeCommon.AirFlowrateRange |  | Pset_AirTerminalOccurrence.AirFlowRate |  | Pset_AirTerminalOccurrence.AirFlowRate
Measured air volume flow |  |  |  |  | X | X | Pset_AirTerminalPHistory.AirFlowRate |  | Pset_AirTerminalPHistory.AirFlowRate |  | Pset_AirTerminalPHistory.AirFlowRate
Air temperature (heating) |  |  |  |  | X | X | Pset_AirTerminalPHistory.SupplyAirTemperatureHeating |  | Pset_AirTerminalPHistory.SupplyAirTemperatureHeating |  | Pset_AirTerminalPHistory.SupplyAirTemperatureHeating
Air temperature (cooling) |  |  |  |  | X | X | Pset_AirTerminalPHistory.SupplyAirTemperatureCooling |  | Pset_AirTerminalPHistory.SupplyAirTemperatureCooling |  | Pset_AirTerminalPHistory.SupplyAirTemperatureCooling
Airflow type |  |  |  |  | X | X | Pset_FlowTerminalAirTerminal.AirflowType |  | Pset_AirTerminalOccurrence.AirflowType |  | Pset_AirTerminalOccurrence.AirflowType
PEB (partial requirements)
Nominal air flow |  |  |  |  | X | X | Pset_AirTerminalTypeCommon.AirFlowrateRange |  | Pset_AirTerminalOccurrence.AirFlowRate |  | Pset_AirTerminalOccurrence.AirFlowRate
Measured air volume flow |  |  |  |  | X | X | Pset_AirTerminalPHistory.AirFlowRate |  | Pset_AirTerminalPHistory.AirFlowRate |  | Pset_AirTerminalPHistory.AirFlowRate
Sanitary/HVAC design (partial requirements)
Nominal air flow |  |  |  | X | X | X | Pset_AirTerminalTypeCommon.AirFlowrateRange |  | Pset_AirTerminalOccurrence.AirFlowRate |  | Pset_AirTerminalOccurrence.AirFlowRate
Airflow type |  |  |  | X | X | X | Pset_FlowTerminalAirTerminal.AirflowType |  | Pset_AirTerminalOccurrence.AirflowType |  | Pset_AirTerminalOccurrence.AirflowType
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B2070 – Exterior Louvers and Vents D3060.10 – Supply Air D3060.20 – Return Air
DIN276 |  | KG431 – Lüftungsanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Ventilation air terminal

## Ventilation duct
Ventilation duct
Return to overview
General
A ventilation duct is a duct serving to distribute air in a building, eventually after treatment (filtering, heating, cooling, humidification, etc.).
Other data sheets for ventilation elements and ducts: ventilation duct connection, fan, filter, air handling unit, air-to-air exchanger, ventilation air terminal, chimney.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Rigid duct |  | IfcDuctSegmentType.RIGIDSEGMENT | [5 empty] | IfcDuctSegment.RIGIDSEGMENT |  | IfcDuctSegment.RIGIDSEGMENT
Flexible duct |  | IfcDuctSegmentType.FLEXIBLESEGMENT | [5 empty] | IfcDuctSegment.FLEXIBLESEGMENT |  | IfcDuctSegment.FLEXIBLESEGMENT
A ventilation network is composed of several types of elements: the IfcFlowSegment (IFC2x3) and the IfcDuctSegment (IFC4) represent only the straight (or flexible) segments
- Elbows, T-fittings and other fittings between sections of different size/shape: The ifcFlowFitting (IFC2x3) and the ifcDuctFitting (IFC4), see duct fitting
- Silencer: IfcFlowTreatmentDevice (IFC2x3) and IfcDuctSilencer (IFC4)
- Various flaps and dampers (non-return, regulating, firebreak, etc.) : IfcFlowController (IFC2x3) and IfcDamper (IFC4)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Global geometry |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Global geometry |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Clash detection (partial requirements)
Global geometry |  |  | X
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Insulation - thickness |  |  |  |  | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_DuctSegmentTypeCommon.Status1 |  | Pset_DuctSegmentTypeCommon.Status |  | Pset_DuctSegmentTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | ePset_DuctSegmentTypeCommon.FireRating1 |  | Pset_DuctSegmentTypeCommon.FireRating |  | Pset_DuctSegmentTypeCommon.FireRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  | X | X
Specifications |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Space requirement schema |  |  | X
Single-line diagram |  |  | X | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3050.50 – HVAC Air Distribution Systems D3060 – Ventilation
DIN276 |  | KG429 – Sonstiges zur KG420 (Wärmeversorgungsanlagen) KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Ventilation duct connection
Ventilation duct connection
Return to overview
General
A ventilation duct is a duct serving to distribute air in a building, eventually after treatment (filtering, heating, cooling, humidification, etc.). A duct fitting includes elbows, section change adapters, T-fittings and other shaped fittings, plugs, etc.
Other sheets for ventilation elements and ducts: ventilation duct, fan, filter, air handling unit, air-to-air exchanger, vent, chimney.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Ventilation duct connection |  | IfcDuctFittingType | [5 empty] | IfcDuctFitting |  | IfcDuctFitting
Connection |  | IfcDuctFittingType.CONNECTOR | [5 empty] | IfcDuctFitting.CONNECTOR |  | IfcDuctFitting.CONNECTOR
Elbow |  | IfcDuctFittingType.BEND | [5 empty] | IfcDuctFitting.BEND |  | IfcDuctFitting.BEND
Junction (Y - T - X) |  | IfcDuctFittingType.JUNCTION | [5 empty] | IfcDuctFitting.JUNCTION |  | IfcDuctFitting.JUNCTION
Shutter |  | IfcDuctFittingType.OBSTRUCTION | [5 empty] | IfcDuctFitting.OBSTRUCTION |  | IfcDuctFitting.OBSTRUCTION
Reducer |  | IfcDuctFittingType.TRANSITION | [5 empty] | IfcDuctFitting.TRANSITION |  | IfcDuctFitting.TRANSITION
Adapter |  | IfcDuctFittingType.TRANSITION | [5 empty] | IfcDuctFitting.TRANSITION |  | IfcDuctFitting.TRANSITION
A ventilation network is comprised of several types of elements:
- Straight or flexible element: IfcFlowSegment (IFC2x3) and l'IfcDuctSegment (IFC4), see ventilation duct
- Elbows, T-fittings and other fittings between sections of different size/shape: The IfcFlowFitting (IFC2x3) and the IfcDuctFitting (IFC4), see present data sheet
- Silencer: IfcFlowTreatmentDevice (IFC2x3) and IfcDuctSilencer (IFC4)
- Various flaps and dampers (non-return, regulating, firebreak, etc.) : IfcFlowController (IFC2x3) and IfcDamper (IFC4)
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Insulation - thickness |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Insulation - thickness |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_DuctFittingTypeCommon.Status1 |  | Pset_DuctFittingTypeCommon.Status |  | Pset_DuctFittingTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_DuctFittingTypeCommon.FireRating |  | Pset_DuctFittingTypeCommon.FireRating |  | Pset_DuctFittingTypeCommon.FireRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Measurement protocol |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  | X | X | X | X
Reports
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3050.50 – HVAC Air Distribution Systems D3060 – Ventilation
DIN276 |  | KG429 – Sonstiges zur KG420 (Wärmeversorgungsanlagen) KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Ventilation duct connection

## Ventilation silencer
Ventilation silencer
Return to overview
General
A ventilation silencer serves to reduce the transmission, through the interior of the duct, of the noise created by the ventilation system components (fan, air movement, etc.) or coming from a room.
Other data sheets for ventilation accessories: fan, air-to-air exchanger, air handling unit, vent, silencer, filter, damper and register.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Oval silencer |  | IfcDuctSilencerType.FLATOVAL | [5 empty] | IfcDuctSilencer.FLATOVAL |  | IfcDuctSilencer.FLATOVAL
Rectangular silencer |  | IfcDuctSilencerType.RECTANGULAR | [5 empty] | IfcDuctSilencer.RECTANGULAR |  | IfcDuctSilencer.RECTANGULAR
Round silencer |  | IfcDuctSilencerType.ROUND | [5 empty] | IfcDuctSilencer.ROUND |  | IfcDuctSilencer.ROUND
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
2D documents (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Inlets and outlets - dimensions |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  |  | X | X | X
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Diameter |  |  |  | X | X | X
Inlets and outlets - dimensions |  |  |  | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  |  | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  |  | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  |  | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  |  | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  |  | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  |  | X | X | X | ePset_DuctSilencerTypeCommon.Status1 |  | Pset_DuctSilencerTypeCommon.Status |  | Pset_DuctSilencerTypeCommon.Status
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  |  | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  |  | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Maintenance (partial requirements)
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Precise calculation |  |  |  | X | X | X
Technical recommendations |  |  |  | X
Specifications |  |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Maintenance log |  |  |  |  | X | X
Plans and diagrams
Single-line diagram |  |  |  | X | X | X
Reports
Performances requirements |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  |  | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | D3060.90 – Ventilation Supplementary Components
DIN276 |  | KG431 – Lüftungsanlagen KG432 – Teilklimaanlagen KG433 – Klimaanlagen KG434 – Kälteanlagen KG475 – Prozesswärme-, kälte- und -luftanlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Ventilation silencer

## Wall
Wall
Return to overview
General
A wall is a flat, vertical (or nearly vertical) partition, either opaque or partially or completely glazed, that divides the spaces of a building (inside spaces/outside spaces/site) vertically. This element may or may not be load-bearing. If it is load-bearing, it consists of a load-bearing structural part which can be in a monolithic material (concrete, masonry, etc.) or of the frame type (wood, metal, etc.). The structural role may differ on a case-by-case basis, including:
- Transferring upper vertical loads to lower elements (walls, columns, beams, foundation)
- Absorbing shear forces in order to horizontally brace a post/slab type building
- Absorbing horizontal thrusts (earth)
The non-load-bearing layers and elements of the wall have different roles:
- Insulation
- Waterproofing
- Interior or exterior finishing
- Other….
Other sheets for vertical walls : curtain wall, wall finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Wall |  | IfcWall.STANDARD | [5 empty] | IfcWall.STANDARD |  | IfcWall.STANDARD
Parapet |  | IfcWall.USERDEFINED[PARAPET] | [5 empty] | IfcWall.PARAPET |  | IfcWall.PARAPET
Load-bearing masonry |  | IfcWall.USERDEFINED[SOLIDWALL] | [5 empty] | IfcWall.SOLIDWALL |  | IfcWall.SOLIDWALL
Bracing masonry |  | IfcWall.SHEAR | [5 empty] | IfcWall.SHEAR |  | IfcWall.SHEAR
Timber frame wall |  | IfcWall.ELEMENTEDWALL | [5 empty] | IfcWall.ELEMENTEDWALL |  | IfcWall.ELEMENTEDWALL
Frost footing |  | IfcWall.USERDEFINED[SOLIDWALL] | [5 empty] | IfcWall.SOLIDWALL |  | IfcWall.SOLIDWALL
Frost wall |  | IfcWall.USERDEFINED[SOLIDWALL] | [5 empty] | IfcWall.SOLIDWALL |  | IfcWall.SOLIDWALL
Partition |  | IfcWall.USERDEFINED[PARTITIONNING] | [5 empty] | IfcWall.PARTITIONING |  | IfcWall.PARTITIONING
Movable wall |  | IfcWall.USERDEFINED[MOVABLE] | [5 empty] | IfcWall.MOVABLE |  | IfcWall.MOVABLE
Thermal break (structural) |  | IfcWall.USERDEFINED[INSULATION] | [5 empty] | IfcWall.USERDEFINED[INSULATION] |  | IfcWall.USERDEFINED[INSULATION]
Insulating masonry |  | IfcWall.USERDEFINED[SOLIDWALL] | [5 empty] | IfcWall.SOLIDWALL |  | IfcWall.SOLIDWALL
Toilet partition |  | IfcWall.STANDARD | [5 empty] | IfcWall.STANDARD |  | IfcWall.STANDARD
Technical space closure |  | IfcWall.PLUMBINGWALL | [5 empty] | IfcWall.PLUMBINGWALL |  | IfcWall.PLUMBINGWALL
Precast concrete wall |  | IfcWall.USERDEFINED[SOLIDWALL] | [5 empty] | IfcWall.SOLIDWALL |  | IfcWall.SOLIDWALL
Secant pile |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Tangeant pile |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Sheet pile |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Retaining wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Deepwall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Diaphragm wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Slurry wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Soldier pile wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Lagging wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Combiwall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Soilmix wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Cement-bentonite slurry wall |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Timbered trench |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
Shored trench |  | IfcWall.USERDEFINED[RETAININGWALL] | [5 empty] | IfcWall.USERDEFINED[RETAININGWALL] |  | IfcWall.USERDEFINED[RETAININGWALL]
When exporting a wall it is possible to export the wall as a whole with all its components (layers, angle irons, skirting boards…), with the components as sub-entities of the global wall. It is also possible to decompose the wall on export, in which case each sub-component is an IFC element in its own right. The sub-components of a wall are:
- Global wall: IfcWall
- Separated-out load-bearing layers: IfcWall – SOLIDWALL
- Separate non-bearing layers IfcWall or IfcCovering (Ifc2x3 and Ifc4) – CLADDING – INSULATION – MEMBRANE
- Skirtingboard, cornice…: IfcCovering (Ifc2x3 and Ifc4) – SKIRTINGBOARD – MOLDING
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Structural design (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Modelling of the lintels |  |  | X | X | X | X
Building permit (partial requirements)
Length |  |  | X
Height |  |  | X
Thickness |  |  | X
Thickness of each layer |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Modelling of the lintels |  |  | X | X | X | X
Precasting (partial requirements)
Length |  |  |  | X | X
Height |  |  |  | X | X
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Heat loss calculation
Length | X |  | X | X
Height | X |  | X | X
Thickness |  |  | X | X
Thickness of each layer |  |  | X | X
Reservations |  |  |  | X
Fire safety (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Architectural design (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Height |  |  | X |  | X
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Modelling of the lintels |  |  |  |  | X
Acoustics (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  |  | X | X | X
Clash detection (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Optional requirements
Steel reinforcement - dimensions |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_WallCommon.Status1 |  | Pset_WallCommon.Status |  | Pset_WallCommon.Status
Renovation status (Archicad) | X |  | X | X | X | X | Pset_WallCommon.Status |  | Pset_WallCommon.Status |  | Pset_WallCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is load-bearing | X |  | X | X | X | X | Pset_WallCommon.LoadBearing |  | Pset_WallCommon.LoadBearing |  | Pset_WallCommon.LoadBearing
Is external | X |  | X | X | X | X | Pset_WallCommon.IsExternal |  | Pset_WallCommon.IsExternal |  | Pset_WallCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Structural design (partial requirements)
Construction method |  |  |  | X | X | X | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X | X | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  |  | X | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Reinforcement ratio |  |  | X |  | X |  | ePset_ConcreteElementGeneral.ReinforcementVolumeRatio1 |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio |  | Pset_ConcreteElementGeneral.ReinforcementVolumeRatio
Thermal transmittance |  |  | X |  | X |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_WallCommon.FireRating |  | Pset_WallCommon.FireRating |  | Pset_WallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance |  | Pset_WallCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  | X | X |  |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_WallCommon.AcousticRating |  | Pset_WallCommon.AcousticRating |  | Pset_WallCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Pre-calculation |  |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Formwork plan |  |  |  | X | X | X
Layout plan |  |  |  | X | X | X
Expansion joints plan |  |  |  | X | X | X
Construction details |  |  |  | X | X | X
Steel reinforcement plan |  |  |  |  | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Stability report |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | A1010.10 – Wall Foundations (Foundation walls) A1020.30 Special Foundation Walls A2010 Walls for Subgrade EnclosuresA4030 - Slab Trenches B2010 Exterior WallB2080.50 – Exterior Balcony Walls and Railings B2090 – Exterior Wall Specialties C1010 – Partitions C2010 – Wall Finishes F1020 – Special Structure
DIN276 |  | 312 – Umschließung 331 – Tragende Außenwände 335 – Außenwändbekleidungen, Außen 336 – Außenwändbekleidungen, Innen 332 – Nichttragende Außenwände 341 – Tragende Innenwände 342 – Nichttragende Innenwände 345 – Innenwändbekleidungen 346 – Elementierte Innenwandkonstruktionen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Wall

## Wall finishing
Wall finishing
Return to overview
General
This sheet contains all the finishing layers for the interior and exterior walls. These are always non-load bearing layers.
Generally, the walls are modelled as multi-layers and the IFC export keeps these multi-layered walls, including the finishes. However, in some cases it is useful to have separate layers, and it is in these cases that the present GID sheet should be used :
- A point finish on a wall, e.g. wall tiling on a partial wall surface, modelled with a single layer "wall" overlaying the full multilayer wall.
- Finishing elements such as skirting boards, mouldings, plinths, etc. modelled with a separate object from the multilayer wall.
- Need to have each layer separated in the IFC model (quantity extraction, work tracking by material, etc.). It is possible to break down layers into individual objects when exporting IFC. Depending on the software you can specify an IFC class and type for each layer (PARTS Revit), the class is fixed in other software (Archicad, Allplan...).
- If the native modelling has been done layer by layer, then the mapping should be specified layer by layer, each layer being an independent IFC object.
Other related sheets : floor finishing, roof finishing, ceiling finishing.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Cladding (metal, cassette, stone,etc.) |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Plaster (plaster, clay, lime, cement,etc.) |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Stone cladding (marble, granite, etc.) |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Tiling |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Masonry cladding |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Carpet |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Finishing panel |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Plasterboard |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Plinth |  | IfcCovering.USERDEFINED[SKIRTINGBOARD] | [5 empty] | IfcCovering.SKIRTINGBOARD |  | IfcCovering.SKIRTINGBOARD
Baseboard |  | IfcCovering.USERDEFINED[SKIRTINGBOARD] | [5 empty] | IfcCovering.SKIRTINGBOARD |  | IfcCovering.SKIRTINGBOARD
Cornice (exterior) |  | IfcCovering.USERDEFINED[MOLDING] | [5 empty] | IfcCovering.MOLDING |  | IfcCovering.MOLDING
Molding (interior) |  | IfcCovering.USERDEFINED[MOLDING] | [5 empty] | IfcCovering.MOLDING |  | IfcCovering.MOLDING
Sandwich panel |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Battens |  | IfcCovering.CLADDING | [5 empty] | IfcCovering.CLADDING |  | IfcCovering.CLADDING
Wall protection |  | IfcCovering.USERDEFINED[SHOCKISOLATOR] | [5 empty] | IfcCovering.USERDEFINED[SHOCKISOLATOR] |  | IfcCovering.USERDEFINED[SHOCKISOLATOR]
Wall painting |  | IfcCovering.USERDEFINED[PAINTING] | [5 empty] | IfcCovering.USERDEFINED[WALL_PAINTING] |  | IfcCovering.USERDEFINED[PAINTING]
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Height |  |  | X
Thickness |  |  | X
Thickness of each layer |  |  | X
PEB (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Precasting (partial requirements)
Length |  |  |  | X | X
Height |  |  |  | X | X
Thickness |  |  |  | X | X
Thickness of each layer |  |  |  | X | X
Peripheral profile |  |  |  | X | X
Reservations |  |  |  | X | X
2D documents (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Architectural design (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Height |  |  | X |  | X
Thickness |  |  | X |  | X
Thickness of each layer |  |  |  |  | X
Acoustics (partial requirements)
Length |  |  | X | X | X | X
Height |  |  | X | X | X | X
Thickness |  |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Clash detection (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Thickness of each layer |  |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Reservations |  |  |  | X | X | X
Rendering (partial requirements)
Length | X |  | X | X | X | X
Height | X |  | X | X | X | X
Thickness | X |  | X | X | X | X
Peripheral profile |  |  |  | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_CoveringCommon.Status1 |  | Pset_CoveringCommon.Status |  | Pset_CoveringCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal |  | Pset_CoveringCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Precasting (partial requirements)
Construction method |  |  |  | X | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
LCA (Life Cycle Analysis)
Construction method |  |  |  |  | X |  | Pset_ConcreteElementGeneral.ConstructionType |  | Pset_ConcreteElementGeneral.ConstructionMethod |  | Pset_ConcreteElementGeneral.ConstructionMethod
Thermal transmittance |  |  | X |  | X |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Is outer shell |  |  |  |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Thermal conductivity |  |  |  |  | X |  | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_CoveringCommon.FireRating |  | Pset_CoveringCommon.FireRating |  | Pset_WallCommon.FireRating
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Building permit (partial requirements)
Thermal transmittance |  |  | X |  |  |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance |  | Pset_CoveringCommon.ThermalTransmittance
Thermal conductivity |  |  | X | X | X | X | ePset_MaterialThermal.ThermalConductivity1 |  | Pset_MaterialThermal.ThermalConductivity |  | Pset_MaterialThermal.ThermalConductivity
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating |  | Pset_CoveringCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Plan of openings |  |  |  | X | X | X
Specific elements plan |  |  |  | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B2010.10 Exterior Wall Veneer C2010 – Wall finishing
DIN276 |  | 335 – Außenwandbekleidungen außen 336 – Außenwandbekleidungen innen 345 – Innenwandbekleidungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Wall finishing

## Water collector
Water collector
Return to overview
General
A gutter is a piping system serving to collect rainwater at the base of the slopes of a roof.
Other sheets for flues : sanitary/heating pipe, sanitary/heating pipe fitting, chimney.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Gutter |  | IfcPipeSegmentType.GUTTER | [5 empty] | IfcPipeSegment.GUTTER |  | IfcPipeSegment.GUTTER
Water channel |  | IfcPipeSegmentType.GUTTER | [5 empty] | IfcPipeSegment.GUTTER |  | IfcPipeSegment.GUTTER
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Building permit (partial requirements)
Length |  |  | X
Width |  |  | X
Height |  |  | X
Diameter |  |  | X
2D documents (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Architectural design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Length |  |  | X |  | X
Width |  |  | X |  | X
Height |  |  | X |  | X
Diameter |  |  | X |  | X
Maintenance (partial requirements)
Length |  |  |  |  | X | X
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Diameter |  |  |  |  | X | X
Clash detection (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Rendering (partial requirements)
Length |  |  | X | X | X | X
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Diameter |  |  | X | X | X | X
Optional requirements
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name |  |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification |  |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status |  |  | X | X | X | X | ePset_PipeSegmentTypeCommon.Status1 |  | Pset_PipeSegmentTypeCommon.Status |  | Pset_PipeSegmentTypeCommon.Status
Renovation status (Archicad) |  |  | X | X | X | X | ePset_PipeSegmentTypeCommon.Status1 |  | Pset_PipeSegmentTypeCommon.Status |  | Pset_PipeSegmentTypeCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external |  |  | X | X | X | X | BIMids_PipeSegmentTypeCommon.IsExternal2 |  | BIMids_PipeSegmentTypeCommon.IsExternal2 |  | BIMids_PipeSegmentTypeCommon.IsExternal2
Is external (Archicad) |  |  | X | X | X | X | BIMids_PipeSegmentTypeCommon.IsExternal2 |  | BIMids_PipeSegmentTypeCommon.IsExternal2 |  | BIMids_PipeSegmentTypeCommon.IsExternal2
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing |  |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation |  |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle |  |  | X
Pre-calculation |  |  | X
Precise calculation |  |  |  | X | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Plans and diagrams
Construction details |  |  |  | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Plans and diagrams
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B3020.70 – Rainwater Management
DIN276 |  | KG 411 – Abwasseranlagen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Window
Window
Return to overview
General
A window is a construction element that serves mainly to bring in natural light and fresh air. It takes the form of vertical openings but also horizontal openings such as roof windows or dome skylights. A window consists of a frame (fixed part) and one or more panels (moving parts), plus accessories such as hinges and pivoting, sliding or folding hardware. It can also incorporate solar protection or occlusion.
Other data sheets for opening elements and items with opening elements as components : door, curtain wall.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Window |  | IfcWindow | [5 empty] | IfcWindow |  | IfcWindow
Skylight dome |  | IfcWindow | [5 empty] | IfcWindow.LIGHTDOME |  | IfcWindow.LIGHTDOME
Roof window |  | IfcWindow | [5 empty] | IfcWindow.LIGHTDOME |  | IfcWindow.LIGHTDOME
Smoke extraction window |  | IfcWindow | [5 empty] | IfcWindow.SKYLIGHT |  | IfcWindow.SKYLIGHT
The components of an IfcWindow are:
- Sun protection integrated or not in the IfcWindow: IfcShadingDevice (IFC4) – JALOUSIE – SHUTTER – AWNING – USERDEFINED – NOTDEFINED
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Access management (partial requirements)
Width |  |  |  | X | X | X
Height |  |  |  | X | X | X
Window frame (fixed) - dimensions |  |  |  | X | X | X
Window panel (mobile) - dimensions |  |  |  | X | X | X
Building permit (partial requirements)
Width |  |  | X
Height |  |  | X
Window frame (fixed) - dimensions |  |  | X
Window panel (mobile) - dimensions |  |  | X
Threshold - dimensions |  |  | X
Stool - dimensions |  |  | X
Shading device box - dimensions |  |  | X
PEB (partial requirements)
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
2D documents (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Heat loss calculation
Width | X |  | X | X
Height | X |  | X | X
Architectural design (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Handicap accessibility (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Width |  |  | X |  | X
Height |  |  | X |  | X
Maintenance (partial requirements)
Width |  |  |  |  | X | X
Height |  |  |  |  | X | X
Representative modelling (manufacturer element) |  |  |  |  | X | X
Window frame (fixed) - dimensions |  |  |  |  | X | X
Window panel (mobile) - dimensions |  |  |  |  | X | X
Threshold - dimensions |  |  |  |  | X | X
Stool - dimensions |  |  |  |  | X | X
Shading device box - dimensions |  |  |  |  | X | X
Acoustics (partial requirements)
Width |  |  | X | X | X | X
Height |  |  | X | X | X | X
Clash detection (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Intrusion and surveillance (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Rendering (partial requirements)
Width | X |  | X | X | X | X
Height | X |  | X | X | X | X
Window frame (fixed) - dimensions |  |  | X | X | X | X
Window panel (mobile) - dimensions |  |  | X | X | X | X
Threshold - dimensions |  |  | X | X | X | X
Stool - dimensions |  |  | X | X | X | X
Shading device box - dimensions |  |  | X | X | X | X
Optional requirements
Representative modelling (manufacturer element) |  |  |  |  | X | X
Accessories and specific elements |  |  |  | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
IFC Type |  |  | X | X | X | X | IfcPredefinedType. |  | IfcPredefinedType. |  | IfcPredefinedType.
IFC Object Type |  |  | X | X | X | X | IfcObjectType. |  | IfcObjectType. |  | IfcObjectType.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | ePset_WindowCommon.Status1 |  | Pset_WindowCommon.Status |  | Pset_WindowCommon.Status
Material |  |  | X | X | X | X | IfcMaterial. |  | IfcMaterial. |  | IfcMaterial.
Is external | X |  | X | X | X | X | Pset_WindowCommon.IsExternal |  | Pset_WindowCommon.IsExternal |  | Pset_WindowCommon.IsExternal
Optional requirements
Numerical identifier |  |  |  |  | X | X | IfcIdentifier. |  | IfcIdentifier. |  | IfcIdentifier.
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2 |  | BIMids_Common.Phasing2
Work package |  |  |  | X | X | X | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2 |  | BIMids_Common.WorkPackage2
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2 |  | BIMids_Common.Documentation2
Fire safety (partial requirements)
Fire rating |  |  | X | X | X | X | Pset_WindowCommon.FireRating |  | Pset_WindowCommon.FireRating |  | Pset_WindowCommon.FireRating
Is emergency exit |  |  | X | X | X | X | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit
Flammability rating |  |  | X | X | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Is mobile shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Maintenance (partial requirements)
Fire rating |  |  |  |  | X | X | Pset_WindowCommon.FireRating |  | Pset_WindowCommon.FireRating |  | Pset_WindowCommon.FireRating
Is emergency exit |  |  |  |  | X | X | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit
Thermal transmittance |  |  |  |  | X | X | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance
Acoustic resistance |  |  |  |  | X | X | Pset_WindowCommon.AcousticRating |  | Pset_WindowCommon.AcousticRating |  | Pset_WindowCommon.AcousticRating
End date of guarantee |  |  |  |  | X | X | ePset_Warranty.WarrantyEndDate1 |  | Pset_Warranty.WarrantyEndDate |  | Pset_Warranty.WarrantyEndDate
Condition - Date of evaluation |  |  |  |  | X | X | ePset_Condition.AssessmentDate1 |  | Pset_Condition.AssessmentDate |  | Pset_Condition.AssessmentDate
Condition - Condition assessed |  |  |  |  | X | X | ePset_Condition.AssessmentCondition1 |  | Pset_Condition.AssessmentCondition |  | Pset_Condition.AssessmentCondition
Flammability rating |  |  |  |  | X | X | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating |  | Pset_CoveringCommon.FlammabilityRating
Solar transmission of glazing |  |  |  |  | X | X | Pset_DoorWindowGlazingType.SolarHeatGainTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance
Glass layers |  |  |  |  | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Glazing area fraction |  |  |  |  | X | X | ePset_DoorWindowGlazingType.GlazingAreaFraction1 |  | Pset_WindowCommon.GlazingAreaFraction |  | Pset_WindowCommon.GlazingAreaFraction
Type of blackout device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Is mobile shading device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  |  |  | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Bulletproof |  |  |  |  | X | X | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2
Access management (partial requirements)
Is emergency exit |  |  |  | X | X | X | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit
Has motorized opening |  |  |  | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Is mobile shading device |  |  |  | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  |  | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Passage width |  |  |  | X | X | X | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2
Building permit (partial requirements)
Is emergency exit |  |  | X |  |  |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit
Thermal transmittance |  |  | X |  |  |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance
Glazing area fraction |  |  | X |  |  |  | ePset_DoorWindowGlazingType.GlazingAreaFraction1 |  | Pset_WindowCommon.GlazingAreaFraction |  | Pset_WindowCommon.GlazingAreaFraction
Intrusion and surveillance (partial requirements)
Is emergency exit |  |  | X | X | X | X | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit |  | Pset_WindowCommon.FireExit
Opening type | X |  | X | X | X | X | BIMids_Window.OpeningType2 |  | BIMids_WindowCommon.OpeningType2 |  | BIMids_WindowCommon.OpeningType2
Bulletproof |  |  |  | X | X | X | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2 |  | BIMids_DoorWindow.BulletProof2
Security rating |  |  |  | X | X | X | Pset_WindowCommon.SecurityRating |  | Pset_WindowCommon.SecurityRating |  | Pset_WindowCommon.SecurityRating
PEB (partial requirements)
Thermal transmittance |  |  | X | X | X | X | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Solar transmission of glazing |  |  | X | X | X | X | Pset_DoorWindowGlazingType.SolarHeatGainTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance |  | Pset_DoorWindowGlazingType.SolarTransmittance
Glass layers |  |  | X | X | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Type of blackout device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Is mobile shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2 |  | BIMids_DoorWindowShadingDevice.Mobile2
Is automatic shading device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2 |  | BIMids_DoorWindowShadingDevice.MechanicalOperated2
Ventilation gap surface |  |  | X | X | X | X | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2
Heat loss calculation
Thermal transmittance | X |  | X | X |  |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance
Is outer shell | X |  | X | X |  |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
LCA (Life Cycle Analysis)
Thermal transmittance |  |  | X |  | X |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance |  | Pset_WindowCommon.ThermalTransmittance
Is outer shell |  |  | X |  | X |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Acoustics (partial requirements)
Acoustic resistance |  |  | X | X | X | X | Pset_WindowCommon.AcousticRating |  | Pset_WindowCommon.AcousticRating |  | Pset_WindowCommon.AcousticRating
Is outer shell |  |  | X | X | X | X | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2 |  | BIMids_Common.OuterShell2
Glass layers |  |  | X | X | X | X | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers |  | Pset_DoorWindowGlazingType.GlassLayers
Architectural design (partial requirements)
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Opening type | X |  | X | X | X | X | BIMids_Window.OpeningType2 |  | BIMids_WindowCommon.OpeningType2 |  | BIMids_WindowCommon.OpeningType2
Type of blackout device |  |  | X | X | X | X | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2 |  | BIMids_DoorWindowShadingDevice.Type2
Has external sill |  |  |  | X | X | X | Pset_DoorWindowGlazingType.HasSillExternal |  | Pset_WindowCommon.HasSillExternal |  | Pset_WindowCommon.HasSillExternal
Has internal sill |  |  |  | X | X | X | Pset_DoorWindowGlazingType.HasSillInternal |  | Pset_WindowCommon.HasSillInternal |  | Pset_WindowCommon.HasSillInternal
Handicap accessibility (partial requirements)
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Electrical design (partial requirements)
Has motorized opening |  |  | X | X | X | X | ePset_DoorCommon.HasDrive1 |  | Pset_DoorCommon.HasDrive |  | Pset_DoorCommon.HasDrive
Rendering (partial requirements)
Passage width |  |  | X | X | X | X | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2 |  | BIMids_DoorWindow.PassageWidth2
Sanitary/HVAC design (partial requirements)
Ventilation gap surface |  |  | X | X | X | X | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2 |  | BIMids_DoorWindow.VentilationGapSurface2
1) ePset : Custom folder and property according to the BuildingSmart definition as it does not exist in the IFC 2x3 scheme.
2) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Descriptions
Construction principle | X |  | X
Shading principle |  |  | X | X
Operation and technical sheets
Technical sheets |  |  |  |  | X | X
Installation instructions |  |  |  |  | X | X
Maintenance instructions |  |  |  |  | X | X
Plans and diagrams
Construction details |  |  |  | X | X | X
Reports
Performances requirements |  |  | X | X | X | X
Energy report |  |  | X | X | X | X
Optional requirements
Descriptions
Representative image |  |  | X | X | X | X
LCA (Life Cycle Analysis)
Reports
Environmental performance declaration |  |  |  |  | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | B2020 – Exterior Windows B3060.10 – Roof Windows and Skylights C1020 – Interior Windows
DIN276 |  | 334 – Außenwandöffnungen 344 – Innenwandöffnungen 352 – Deckenöffnungen 362 – Dachöffnungen
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available

## Zone
Zone
Return to overview
General
A zone is a group of spaces and/or zones that generally share common properties in terms of use and/or performance requirements. Zones can be inside or outside. The grouping can be, for example, by wing, by department, by housing unit (1 apartment = 1 zone), by temperature setpoint zone, etc.
It should be noted that zones are optional objects that are not mandatory in a BIM project.
Other data sheets for spatial organisation : building, space.
IFC class and type
ELEMENT |  | IFC 2X3 TC1 | [5 empty] | IFC 4 ADD2 |  | IFC 4.3
Zone |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
Wing |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
Appartment |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
Block |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
Group |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
Unit (hospital) |  | IfcZone | [5 empty] | IfcZone |  | IfcZone
At the IFC level, a space can belong to several zones. On the other hand, there is no hierarchical structure.
GID level (Geometry - Information - Documentation)
Important : the geometry table specifies what is required physically in the model at some point. This is not related to the qto which are alphanumerical information based on quantities.
GEOMETRICAL INFORMATION
ELEMENT | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
PEB (partial requirements)
Height |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
2D documents (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Architectural design (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Sanitary/HVAC design (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Maintenance (partial requirements)
Height |  |  |  |  | X | X
Perimeter |  |  |  |  | X | X
Acoustics (partial requirements)
Height |  |  | X | X | X | X
Perimeter |  |  | X | X | X | X
Clash detection (partial requirements)
Height | X |  | X | X | X | X
Perimeter | X |  | X | X | X | X
Rendering (partial requirements)
Perimeter | X |  | X | X | X | X
ALPHANUMERICAL INFORMATION
PROPERTY | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE | IFC 2X3 TC1 |  | IFC 4 ADD2 |  | IFC 4.3
Minimum requirements
Object name | X |  | X | X | X | X | IfcName. |  | IfcName. |  | IfcName.
Classification | X |  | X | X | X | X | IfcClassification. |  | IfcClassification. |  | IfcClassification.
Status | X |  | X | X | X | X | BIMids_Common.Status1 |  | BIMids_Common.Status1 |  | BIMids_Common.Status1
Phasing | [5 empty] | X | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1
Optional requirements
Phasing | X |  | X | X | X | X | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1 |  | BIMids_Common.Phasing1
Documentation | X |  | X | X | X | X | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1 |  | BIMids_Common.Documentation1
1) BIMids : Customised folder and property according to the BIMids definition as not existing in the IFC schemas.
The quantities supported by the IFC schema are called IfcQuantitySet. These quantities are interpreted according to their name attribute and classified according to their measurement type. They are automatically calculated and exported to the IFC file. It is therefore an alphanumeric property which includes certain geometric data (not to be confused with the geometry table). List of IFC4 Qto.
DOCUMENTATION
DOCUMENT TYPE | PHASE1 PD |  | PHASE2 FD/AUT | PHASE3 FP/TEND | PHASE4 EXE/ASB | PHASE5 OPE
Minimum requirements
Plans and diagrams
Space planning diagram | X
Reports
Energy report |  |  | X | X | X | X
Tables
Zone data sheet | X |  | X | X | X | X
List of rooms | X |  | X | X | X | X
Classification
CLASSIFICATION
CLASSIFICATION |  | NUMBER - DESCRIPTION
Uniformat II 2010 |  | None
DIN276 |  | None
TechBiM and MatBiM links
You will find here a link to the TechBiM/MatBiM documentation.
Link not available